## Interfaces
InterfaceCode | InterfaceName | InterfaceType | InterfaceAddress | Port | Enable
接口编号 | 接口名称 | 接口类型 | 接口地址 | 端口 | 启用
If_1 | 网关_1号楼 | IpTunneling | 192.168.4.241 | 3671 | TRUE
If_2 | 网关_3号楼 | IpTunneling | 192.168.4.242 | 3671 | TRUE
If_3 | 网关_地下车库 | IpTunneling | 192.168.4.243 | 3671 | TRUE
Note on D1: 默认广播IP：224.0.23.12

## Areas
MainCode | MainArea | MiddleCode | MiddleArea | SubCode | SubArea | AreaCode
主区域编号 | 主区域名称 | 中区域编号 | 中区域名称 | 子区域编号 | 子区域名称 | 区域编号
Bld01 | 1号楼 |  |  |  |  | Bld01
Bld01 | 1号楼 | B02 | B02 |  |  | Bld01.B02
Bld01 | 1号楼 | B01 | B01 |  |  | Bld01.B01
Bld01 | 1号楼 | F01 | F01 |  |  | Bld01.F01
Bld01 | 1号楼 | F02 | F02 |  |  | Bld01.F02
Bld01 | 1号楼 | F02 | F02 | F02A | F02AAA | Bld01.F02.F02A
Bld01 | 1号楼 | F03 | F03 |  |  | Bld01.F03
Bld01 | 1号楼 | F03 | F03 | F03A | F03AAA | Bld01.F03.F03A
Bld01 | 1号楼 | F04 | F04 |  |  | Bld01.F04
Bld01 | 1号楼 | F05 | F05 |  |  | Bld01.F05
Bld01 | 1号楼 | F06 | F06 |  |  | Bld01.F06
Bld01 | 1号楼 | F07 | F07 |  |  | Bld01.F07
Bld01 | 1号楼 | F08 | F08 |  |  | Bld01.F08
Bld01 | 1号楼 | F09 | F09 |  |  | Bld01.F09
Bld01 | 1号楼 | F10 | F10 |  |  | Bld01.F10
Bld01 | 1号楼 | F11 | F11 |  |  | Bld01.F11
Bld01 | 1号楼 | F12 | F12 |  |  | Bld01.F12
Bld01 | 1号楼 | F13 | F13 |  |  | Bld01.F13
Bld01 | 1号楼 | F14 | F14 |  |  | Bld01.F14
Bld01 | 1号楼 | F15 | F15 |  |  | Bld01.F15
Bld03 | 3号楼 |  |  |  |  | Bld03
Bld03 | 3号楼 | F01 | F01 |  |  | Bld03.F01
Bld03 | 3号楼 | F02 | F02 |  |  | Bld03.F02
Bld03 | 3号楼 | F03 | F03 |  |  | Bld03.F03
Bld03 | 3号楼 | F04 | F04 |  |  | Bld03.F04
Bld06 | 6号楼 |  |  |  |  | Bld06
Bld06 | 6号楼 | F01 | F01 |  |  | Bld06.F01
Garage | 车库 |  |  |  |  | Garage

## Objects
AreaCode | InterfaceCode | ObjectCode | ObjectType | ObjectName | Sw_GrpDpt | Sw_Ctl_GrpAddr | Sw_Fdb_GrpAddr | Val_GrpDpt | Val_Ctl_GrpAddr | Val_Fdb_GrpAddr
区域编号 | 接口编号 | 对象编号 | 对象类型 | 对象名称 | 开关-地址类型 | 开关-控制地址 | 开关-反馈地址 | 数值-地址类型 | 数值-控制地址 | 数值-反馈地址
Garage |  | gB01_Scd.En | EnableCtl | [地下车库]定时启用 | 1.003: enable | 0/0/220
Garage |  | gB01_Actr.Lock | EnableCtl | [地下车库]执行器锁定 | 1.002: boolean | 0/0/230
Garage |  | gB01_Pb.Lock | EnableCtl | [地下车库]面板锁定 | 1.002: boolean | 0/0/240
Garage |  | gB01_B1-6AT1_01.Ctl | Switch |  | 1.001: switch | 0/1/1 | 0/1/101
Garage |  | gB01_B1-6AT1_02.Ctl | Switch |  | 1.001: switch | 0/1/2 | 0/1/102
Garage |  | gB01_B1-6AT1_03.Ctl | Switch |  | 1.001: switch | 0/1/3 | 0/1/103
Garage |  | gB01_B1-6AT1_04.Ctl | Switch |  | 1.001: switch | 0/1/4 | 0/1/104
Garage |  | gB01_B1-6AT1_05.Ctl | Switch |  | 1.001: switch | 0/1/5 | 0/1/105
Garage |  | gB01_B1-6AT1_06.Ctl | Switch |  | 1.001: switch | 0/1/6 | 0/1/106
Garage |  | gB01_B1-6AT1_07.Ctl | Switch |  | 1.001: switch | 0/1/7 | 0/1/107
Garage |  | gB01_B1-6AT1_08.Ctl | Switch |  | 1.001: switch | 0/1/8 | 0/1/108
Garage |  | gB01_B1-6AT2_01.Ctl | Switch |  | 1.001: switch | 0/1/21 | 0/1/121
Garage |  | gB01_B1-6AT2_02.Ctl | Switch |  | 1.001: switch | 0/1/22 | 0/1/122
Garage |  | gB01_B1-6AT2_03.Ctl | Switch |  | 1.001: switch | 0/1/23 | 0/1/123
Garage |  | gB01_B1-6AT2_04.Ctl | Switch |  | 1.001: switch | 0/1/24 | 0/1/124
Garage |  | gB01_B1-6AT2_05.Ctl | Switch |  | 1.001: switch | 0/1/25 | 0/1/125
Garage |  | gB01_B1-6AT2_06.Ctl | Switch |  | 1.001: switch | 0/1/26 | 0/1/126
Garage |  | gB01_B1-6AT2_07.Ctl | Switch |  | 1.001: switch | 0/1/27 | 0/1/127
Garage |  | gB01_B1-6AT2_08.Ctl | Switch |  | 1.001: switch | 0/1/28 | 0/1/128
Garage |  | gB01_B1-6AT2_09.Ctl | Switch |  | 1.001: switch | 0/1/29 | 0/1/129
Garage |  | gB01_B1-6AT2_10.Ctl | Switch |  | 1.001: switch | 0/1/30 | 0/1/130
Garage |  | gB01_B1-6AT2_11.Ctl | Switch |  | 1.001: switch | 0/1/31 | 0/1/131
Garage |  | gB01_B1-6AT2_12.Ctl | Switch |  | 1.001: switch | 0/1/32 | 0/1/132
Garage |  | gB01_B1-8AT_01.Ctl | Switch |  | 1.001: switch | 0/1/41 | 0/1/141
Garage |  | gB01_B1-8AT_02.Ctl | Switch |  | 1.001: switch | 0/1/42 | 0/1/142
Garage |  | gB01_B1-8AT_03.Ctl | Switch |  | 1.001: switch | 0/1/43 | 0/1/143
Garage |  | gB01_B1-8AT_04.Ctl | Switch |  | 1.001: switch | 0/1/44 | 0/1/144
Garage |  | gB01_B1-8AT_05.Ctl | Switch |  | 1.001: switch | 0/1/45 | 0/1/145
Garage |  | gB01_B1-8AT_06.Ctl | Switch |  | 1.001: switch | 0/1/46 | 0/1/146
Garage |  | gB01_B1-8AT_07.Ctl | Switch |  | 1.001: switch | 0/1/47 | 0/1/147
Garage |  | gB01_B1-8AT_08.Ctl | Switch |  | 1.001: switch | 0/1/48 | 0/1/148
Garage |  | gB01_B1-9AL_01.Ctl | Switch |  | 1.001: switch | 0/1/61 | 0/1/161
Garage |  | gB01_B1-9AL_02.Ctl | Switch |  | 1.001: switch | 0/1/62 | 0/1/162
Garage |  | gB01_B1-9AL_03.Ctl | Switch |  | 1.001: switch | 0/1/63 | 0/1/163
Garage |  | gB01_B1-9AL_04.Ctl | Switch |  | 1.001: switch | 0/1/64 | 0/1/164
Garage |  | gB01_B1-9AL_05.Ctl | Switch |  | 1.001: switch | 0/1/65 | 0/1/165
Garage |  | gB01_B1-9AL_06.Ctl | Switch |  | 1.001: switch | 0/1/66 | 0/1/166
Garage |  | gB01_B1-9AL_07.Ctl | Switch |  | 1.001: switch | 0/1/67 | 0/1/167
Garage |  | gB01_B1-9AL_08.Ctl | Switch |  | 1.001: switch | 0/1/68 | 0/1/168
Garage |  | gB01_B1-6AT1_Scd.En | EnableCtl | [地下车库]定时_B1-6AT1 | 1.003: enable | 0/1/221
Garage |  | gB01_B1-6AT2_Scd.En | EnableCtl | [地下车库]定时_B1-6AT2 | 1.003: enable | 0/1/222
Garage |  | gB01_B1-8AT_Scd.En | EnableCtl | [地下车库]定时_B1-8AT | 1.003: enable | 0/1/223
Garage |  | gB01_B1-9AL_Scd.En | EnableCtl | [地下车库]定时_B1-9AL | 1.003: enable | 0/1/224
Garage |  | gB01_B1-6AT1_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-6AT1 | 1.002: boolean | 0/1/231
Garage |  | gB01_B1-6AT2_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-6AT2 | 1.002: boolean | 0/1/232
Garage |  | gB01_B1-8AT_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-8AT | 1.002: boolean | 0/1/233
Garage |  | gB01_B1-9AL_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-9AL | 1.002: boolean | 0/1/234
Garage |  | gB01_B1-6AT1_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-6AT1 | 1.002: boolean | 0/1/241
Garage |  | gB01_B1-6AT2_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-6AT2 | 1.002: boolean | 0/1/242
Garage |  | gB01_B1-8AT_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-8AT | 1.002: boolean | 0/1/243
Garage |  | gB01_B1-9AL_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-9AL | 1.002: boolean | 0/1/244
Garage |  | gB01_B1-10AT_01.Ctl | Switch |  | 1.001: switch | 0/2/1 | 0/2/101
Garage |  | gB01_B1-10AT_02.Ctl | Switch |  | 1.001: switch | 0/2/2 | 0/2/102
Garage |  | gB01_B1-10AT_03.Ctl | Switch |  | 1.001: switch | 0/2/3 | 0/2/103
Garage |  | gB01_B1-10AT_04.Ctl | Switch |  | 1.001: switch | 0/2/4 | 0/2/104
Garage |  | gB01_B1-10AT_05.Ctl | Switch |  | 1.001: switch | 0/2/5 | 0/2/105
Garage |  | gB01_B1-10AT_06.Ctl | Switch |  | 1.001: switch | 0/2/6 | 0/2/106
Garage |  | gB01_B1-10AT_07.Ctl | Switch |  | 1.001: switch | 0/2/7 | 0/2/107
Garage |  | gB01_B1-10AT_08.Ctl | Switch |  | 1.001: switch | 0/2/8 | 0/2/108
Garage |  | gB01_B1-11AT1_01.Ctl | Switch |  | 1.001: switch | 0/2/21 | 0/2/121
Garage |  | gB01_B1-11AT1_02.Ctl | Switch |  | 1.001: switch | 0/2/22 | 0/2/122
Garage |  | gB01_B1-11AT1_03.Ctl | Switch |  | 1.001: switch | 0/2/23 | 0/2/123
Garage |  | gB01_B1-11AT1_04.Ctl | Switch |  | 1.001: switch | 0/2/24 | 0/2/124
Garage |  | gB01_B1-11AT1_05.Ctl | Switch |  | 1.001: switch | 0/2/25 | 0/2/125
Garage |  | gB01_B1-11AT1_06.Ctl | Switch |  | 1.001: switch | 0/2/26 | 0/2/126
Garage |  | gB01_B1-11AT1_07.Ctl | Switch |  | 1.001: switch | 0/2/27 | 0/2/127
Garage |  | gB01_B1-11AT1_08.Ctl | Switch |  | 1.001: switch | 0/2/28 | 0/2/128
Garage |  | gB01_B1-11AT2_01.Ctl | Switch |  | 1.001: switch | 0/2/41 | 0/2/141
Garage |  | gB01_B1-11AT2_02.Ctl | Switch |  | 1.001: switch | 0/2/42 | 0/2/142
Garage |  | gB01_B1-11AT2_03.Ctl | Switch |  | 1.001: switch | 0/2/43 | 0/2/143
Garage |  | gB01_B1-11AT2_04.Ctl | Switch |  | 1.001: switch | 0/2/44 | 0/2/144
Garage |  | gB01_B1-11AT2_05.Ctl | Switch |  | 1.001: switch | 0/2/45 | 0/2/145
Garage |  | gB01_B1-11AT2_06.Ctl | Switch |  | 1.001: switch | 0/2/46 | 0/2/146
Garage |  | gB01_B1-11AT2_07.Ctl | Switch |  | 1.001: switch | 0/2/47 | 0/2/147
Garage |  | gB01_B1-11AT2_08.Ctl | Switch |  | 1.001: switch | 0/2/48 | 0/2/148
Garage |  | gB01_B1-16AT_01.Ctl | Switch |  | 1.001: switch | 0/2/61 | 0/2/161
Garage |  | gB01_B1-16AT_02.Ctl | Switch |  | 1.001: switch | 0/2/62 | 0/2/162
Garage |  | gB01_B1-16AT_03.Ctl | Switch |  | 1.001: switch | 0/2/63 | 0/2/163
Garage |  | gB01_B1-16AT_04.Ctl | Switch |  | 1.001: switch | 0/2/64 | 0/2/164
Garage |  | gB01_B1-16AT_05.Ctl | Switch |  | 1.001: switch | 0/2/65 | 0/2/165
Garage |  | gB01_B1-16AT_06.Ctl | Switch |  | 1.001: switch | 0/2/66 | 0/2/166
Garage |  | gB01_B1-16AT_07.Ctl | Switch |  | 1.001: switch | 0/2/67 | 0/2/167
Garage |  | gB01_B1-16AT_08.Ctl | Switch |  | 1.001: switch | 0/2/68 | 0/2/168
Garage |  | gB01_B1-10AT_Scd.En | EnableCtl | [地下车库]定时_B1-10AT | 1.003: enable | 0/2/221
Garage |  | gB01_B1-11AT1_Scd.En | EnableCtl | [地下车库]定时_B1-11AT1 | 1.003: enable | 0/2/222
Garage |  | gB01_B1-11AT2_Scd.En | EnableCtl | [地下车库]定时_B1-11AT2 | 1.003: enable | 0/2/223
Garage |  | gB01_B1-16AT_Scd.En | EnableCtl | [地下车库]定时_B1-16AT | 1.003: enable | 0/2/224
Garage |  | gB01_B1-10AT_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-10AT | 1.002: boolean | 0/2/231
Garage |  | gB01_B1-11AT1_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-11AT1 | 1.002: boolean | 0/2/232
Garage |  | gB01_B1-11AT2_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-11AT2 | 1.002: boolean | 0/2/233
Garage |  | gB01_B1-16AT_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-16AT | 1.002: boolean | 0/2/234
Garage |  | gB01_B1-10AT_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-10AT | 1.002: boolean | 0/2/241
Garage |  | gB01_B1-11AT1_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-11AT1 | 1.002: boolean | 0/2/242
Garage |  | gB01_B1-11AT2_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-11AT2 | 1.002: boolean | 0/2/243
Garage |  | gB01_B1-16AT_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-16AT | 1.002: boolean | 0/2/244
Garage |  | gB01_B1-18AT_01.Ctl | Switch |  | 1.001: switch | 0/3/1 | 0/3/101
Garage |  | gB01_B1-18AT_02.Ctl | Switch |  | 1.001: switch | 0/3/2 | 0/3/102
Garage |  | gB01_B1-18AT_03.Ctl | Switch |  | 1.001: switch | 0/3/3 | 0/3/103
Garage |  | gB01_B1-18AT_04.Ctl | Switch |  | 1.001: switch | 0/3/4 | 0/3/104
Garage |  | gB01_B1-18AT_05.Ctl | Switch |  | 1.001: switch | 0/3/5 | 0/3/105
Garage |  | gB01_B1-18AT_06.Ctl | Switch |  | 1.001: switch | 0/3/6 | 0/3/106
Garage |  | gB01_B1-18AT_07.Ctl | Switch |  | 1.001: switch | 0/3/7 | 0/3/107
Garage |  | gB01_B1-18AT_08.Ctl | Switch |  | 1.001: switch | 0/3/8 | 0/3/108
Garage |  | gB01_B1-19AT_01.Ctl | Switch |  | 1.001: switch | 0/3/21 | 0/3/121
Garage |  | gB01_B1-19AT_02.Ctl | Switch |  | 1.001: switch | 0/3/22 | 0/3/122
Garage |  | gB01_B1-19AT_03.Ctl | Switch |  | 1.001: switch | 0/3/23 | 0/3/123
Garage |  | gB01_B1-19AT_04.Ctl | Switch |  | 1.001: switch | 0/3/24 | 0/3/124
Garage |  | gB01_B1-19AT_05.Ctl | Switch |  | 1.001: switch | 0/3/25 | 0/3/125
Garage |  | gB01_B1-19AT_06.Ctl | Switch |  | 1.001: switch | 0/3/26 | 0/3/126
Garage |  | gB01_B1-19AT_07.Ctl | Switch |  | 1.001: switch | 0/3/27 | 0/3/127
Garage |  | gB01_B1-19AT_08.Ctl | Switch |  | 1.001: switch | 0/3/28 | 0/3/128
Garage |  | gB01_B1-22AT1_01.Ctl | Switch |  | 1.001: switch | 0/3/41 | 0/3/141
Garage |  | gB01_B1-22AT1_02.Ctl | Switch |  | 1.001: switch | 0/3/42 | 0/3/142
Garage |  | gB01_B1-22AT1_03.Ctl | Switch |  | 1.001: switch | 0/3/43 | 0/3/143
Garage |  | gB01_B1-22AT1_04.Ctl | Switch |  | 1.001: switch | 0/3/44 | 0/3/144
Garage |  | gB01_B1-22AT1_05.Ctl | Switch |  | 1.001: switch | 0/3/45 | 0/3/145
Garage |  | gB01_B1-22AT1_06.Ctl | Switch |  | 1.001: switch | 0/3/46 | 0/3/146
Garage |  | gB01_B1-22AT1_07.Ctl | Switch |  | 1.001: switch | 0/3/47 | 0/3/147
Garage |  | gB01_B1-22AT1_08.Ctl | Switch |  | 1.001: switch | 0/3/48 | 0/3/148
Garage |  | gB01_B1-22AT2_01.Ctl | Switch |  | 1.001: switch | 0/3/61 | 0/3/161
Garage |  | gB01_B1-22AT2_02.Ctl | Switch |  | 1.001: switch | 0/3/62 | 0/3/162
Garage |  | gB01_B1-22AT2_03.Ctl | Switch |  | 1.001: switch | 0/3/63 | 0/3/163
Garage |  | gB01_B1-22AT2_04.Ctl | Switch |  | 1.001: switch | 0/3/64 | 0/3/164
Garage |  | gB01_B1-22AT2_05.Ctl | Switch |  | 1.001: switch | 0/3/65 | 0/3/165
Garage |  | gB01_B1-22AT2_06.Ctl | Switch |  | 1.001: switch | 0/3/66 | 0/3/166
Garage |  | gB01_B1-22AT2_07.Ctl | Switch |  | 1.001: switch | 0/3/67 | 0/3/167
Garage |  | gB01_B1-22AT2_08.Ctl | Switch |  | 1.001: switch | 0/3/68 | 0/3/168
Garage |  | gB01_B1-18AT_Scd.En | EnableCtl | [地下车库]定时_B1-18AT | 1.003: enable | 0/3/221
Garage |  | gB01_B1-19AT_Scd.En | EnableCtl | [地下车库]定时_B1-19AT | 1.003: enable | 0/3/222
Garage |  | gB01_B1-22AT1_Scd.En | EnableCtl | [地下车库]定时_B1-22AT1 | 1.003: enable | 0/3/223
Garage |  | gB01_B1-22AT2_Scd.En | EnableCtl | [地下车库]定时_B1-22AT2 | 1.003: enable | 0/3/224
Garage |  | gB01_B1-18AT_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-18AT | 1.002: boolean | 0/3/231
Garage |  | gB01_B1-19AT_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-19AT | 1.002: boolean | 0/3/232
Garage |  | gB01_B1-22AT1_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-22AT1 | 1.002: boolean | 0/3/233
Garage |  | gB01_B1-22AT2_Actr.Lock | EnableCtl | [地下车库]执行器锁定_B1-22AT2 | 1.002: boolean | 0/3/234
Garage |  | gB01_B1-18AT_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-18AT | 1.002: boolean | 0/3/241
Garage |  | gB01_B1-19AT_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-19AT | 1.002: boolean | 0/3/242
Garage |  | gB01_B1-22AT1_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-22AT1 | 1.002: boolean | 0/3/243
Garage |  | gB01_B1-22AT2_Pb.Lock | EnableCtl | [地下车库]面板锁定_B1-22AT2 | 1.002: boolean | 0/3/244
Bld01 |  | 1_Scd.En | EnableCtl | [1号楼]定时_全部 | 1.003: enable | 1/0/220
Bld01 |  | 1_Actr.Lock | EnableCtl | [1号楼]执行器锁定_全部 | 1.002: boolean | 1/0/230
Bld01 |  | 1_Pb.Lock | EnableCtl | [1号楼]面板锁定_全部 | 1.002: boolean | 1/0/240
Bld01.F01 |  | 1F01_1-1AT_01.Ctl | Switch |  | 1.001: switch | 1/1/1 | 1/1/101
Bld01.F01 |  | 1F01_1-1AT_02.Ctl | Switch |  | 1.001: switch | 1/1/2 | 1/1/102
Bld01.F01 |  | 1F01_1-1AT_03.Ctl | Switch |  | 1.001: switch | 1/1/3 | 1/1/103
Bld01.F01 |  | 1F01_1-1AT_04.Ctl | Switch |  | 1.001: switch | 1/1/4 | 1/1/104
Bld01.F01 |  | 1F01_1-1AT_05.Ctl | Switch |  | 1.001: switch | 1/1/5 | 1/1/105
Bld01.F01 |  | 1F01_1-1AT_06.Ctl | Switch |  | 1.001: switch | 1/1/6 | 1/1/106
Bld01.F01 |  | 1F01_1-1AT_07.Ctl | Switch |  | 1.001: switch | 1/1/7 | 1/1/107
Bld01.F01 |  | 1F01_1-1AT_08.Ctl | Switch |  | 1.001: switch | 1/1/8 | 1/1/108
Bld01.F01 |  | 1F01_1-1AT_09.Ctl | Switch |  | 1.001: switch | 1/1/9 | 1/1/109
Bld01.F01 |  | 1F01_1-1AT_10.Ctl | Switch |  | 1.001: switch | 1/1/10 | 1/1/110
Bld01.F01 |  | 1F01_1-1AT_11.Ctl | Switch |  | 1.001: switch | 1/1/11 | 1/1/111
Bld01.F01 |  | 1F01_1-1AT_12.Ctl | Switch |  | 1.001: switch | 1/1/12 | 1/1/112
Bld01.F02 |  | 1F02_1-2GGAL_01.Ctl | Switch |  | 1.001: switch | 1/1/21 | 1/1/121
Bld01.F02 |  | 1F02_1-2GGAL_02.Ctl | Switch |  | 1.001: switch | 1/1/22 | 1/1/122
Bld01.F02 |  | 1F02_1-2GGAL_03.Ctl | Switch |  | 1.001: switch | 1/1/23 | 1/1/123
Bld01.F02 |  | 1F02_1-2GGAL_04.Ctl | Switch |  | 1.001: switch | 1/1/24 | 1/1/124
Bld01.F02 |  | 1F02_1-2GGAL_05.Ctl | Switch |  | 1.001: switch | 1/1/25 | 1/1/125
Bld01.F02 |  | 1F02_1-2GGAL_06.Ctl | Switch |  | 1.001: switch | 1/1/26 | 1/1/126
Bld01.F02 |  | 1F02_1-2GGAL_07.Ctl | Switch |  | 1.001: switch | 1/1/27 | 1/1/127
Bld01.F02 |  | 1F02_1-2GGAL_08.Ctl | Switch |  | 1.001: switch | 1/1/28 | 1/1/128
Bld01.F03 |  | 1F03_1-3GGAL_01.Ctl | Switch |  | 1.001: switch | 1/1/41 | 1/1/141
Bld01.F03 |  | 1F03_1-3GGAL_02.Ctl | Switch |  | 1.001: switch | 1/1/42 | 1/1/142
Bld01.F03 |  | 1F03_1-3GGAL_03.Ctl | Switch |  | 1.001: switch | 1/1/43 | 1/1/143
Bld01.F03 |  | 1F03_1-3GGAL_04.Ctl | Switch |  | 1.001: switch | 1/1/44 | 1/1/144
Bld01.F03 |  | 1F03_1-3GGAL_05.Ctl | Switch |  | 1.001: switch | 1/1/45 | 1/1/145
Bld01.F03 |  | 1F03_1-3GGAL_06.Ctl | Switch |  | 1.001: switch | 1/1/46 | 1/1/146
Bld01.F03 |  | 1F03_1-3GGAL_07.Ctl | Switch |  | 1.001: switch | 1/1/47 | 1/1/147
Bld01.F03 |  | 1F03_1-3GGAL_08.Ctl | Switch |  | 1.001: switch | 1/1/48 | 1/1/148
Bld01.F04 |  | 1F04_1-4GGAL_01.Ctl | Switch |  | 1.001: switch | 1/1/61 | 1/1/161
Bld01.F04 |  | 1F04_1-4GGAL_02.Ctl | Switch |  | 1.001: switch | 1/1/62 | 1/1/162
Bld01.F04 |  | 1F04_1-4GGAL_03.Ctl | Switch |  | 1.001: switch | 1/1/63 | 1/1/163
Bld01.F04 |  | 1F04_1-4GGAL_04.Ctl | Switch |  | 1.001: switch | 1/1/64 | 1/1/164
Bld01.F04 |  | 1F04_1-4GGAL_05.Ctl | Switch |  | 1.001: switch | 1/1/65 | 1/1/165
Bld01.F04 |  | 1F04_1-4GGAL_06.Ctl | Switch |  | 1.001: switch | 1/1/66 | 1/1/166
Bld01.F04 |  | 1F04_1-4GGAL_07.Ctl | Switch |  | 1.001: switch | 1/1/67 | 1/1/167
Bld01.F04 |  | 1F04_1-4GGAL_08.Ctl | Switch |  | 1.001: switch | 1/1/68 | 1/1/168
Bld01.F05 |  | 1F05_1-5GGAL_01.Ctl | Switch |  | 1.001: switch | 1/1/81 | 1/1/181
Bld01.F05 |  | 1F05_1-5GGAL_02.Ctl | Switch |  | 1.001: switch | 1/1/82 | 1/1/182
Bld01.F05 |  | 1F05_1-5GGAL_03.Ctl | Switch |  | 1.001: switch | 1/1/83 | 1/1/183
Bld01.F05 |  | 1F05_1-5GGAL_04.Ctl | Switch |  | 1.001: switch | 1/1/84 | 1/1/184
Bld01.F05 |  | 1F05_1-5GGAL_05.Ctl | Switch |  | 1.001: switch | 1/1/85 | 1/1/185
Bld01.F05 |  | 1F05_1-5GGAL_06.Ctl | Switch |  | 1.001: switch | 1/1/86 | 1/1/186
Bld01.F05 |  | 1F05_1-5GGAL_07.Ctl | Switch |  | 1.001: switch | 1/1/87 | 1/1/187
Bld01.F05 |  | 1F05_1-5GGAL_08.Ctl | Switch |  | 1.001: switch | 1/1/88 | 1/1/188
Bld01.F01 |  | 1F01_Scd.En | EnableCtl | [1号楼]定时_F01 | 1.003: enable | 1/1/221
Bld01.F02 |  | 1F02_Scd.En | EnableCtl | [1号楼]定时_F02 | 1.003: enable | 1/1/222
Bld01.F03 |  | 1F03_Scd.En | EnableCtl | [1号楼]定时_F03 | 1.003: enable | 1/1/223
Bld01.F04 |  | 1F04_Scd.En | EnableCtl | [1号楼]定时_F04 | 1.003: enable | 1/1/224
Bld01.F05 |  | 1F05_Scd.En | EnableCtl | [1号楼]定时_F05 | 1.003: enable | 1/1/225
Bld01.F01 |  | 1F01_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F01 | 1.002: boolean | 1/1/231
Bld01.F02 |  | 1F02_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F02 | 1.002: boolean | 1/1/232
Bld01.F03 |  | 1F03_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F03 | 1.002: boolean | 1/1/233
Bld01.F04 |  | 1F04_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F04 | 1.002: boolean | 1/1/234
Bld01.F05 |  | 1F05_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F05 | 1.002: boolean | 1/1/235
Bld01.F01 |  | 1F01_Pb.Lock | EnableCtl | [1号楼]面板锁定_F01 | 1.002: boolean | 1/1/241
Bld01.F02 |  | 1F02_Pb.Lock | EnableCtl | [1号楼]面板锁定_F02 | 1.002: boolean | 1/1/242
Bld01.F03 |  | 1F03_Pb.Lock | EnableCtl | [1号楼]面板锁定_F03 | 1.002: boolean | 1/1/243
Bld01.F04 |  | 1F04_Pb.Lock | EnableCtl | [1号楼]面板锁定_F04 | 1.002: boolean | 1/1/244
Bld01.F05 |  | 1F05_Pb.Lock | EnableCtl | [1号楼]面板锁定_F05 | 1.002: boolean | 1/1/245
Bld01.F06 |  | 1F06_1-6GGAL_01.Ctl | Switch |  | 1.001: switch | 1/2/1 | 1/2/101
Bld01.F06 |  | 1F06_1-6GGAL_02.Ctl | Switch |  | 1.001: switch | 1/2/2 | 1/2/102
Bld01.F06 |  | 1F06_1-6GGAL_03.Ctl | Switch |  | 1.001: switch | 1/2/3 | 1/2/103
Bld01.F06 |  | 1F06_1-6GGAL_04.Ctl | Switch |  | 1.001: switch | 1/2/4 | 1/2/104
Bld01.F06 |  | 1F06_1-6GGAL_05.Ctl | Switch |  | 1.001: switch | 1/2/5 | 1/2/105
Bld01.F06 |  | 1F06_1-6GGAL_06.Ctl | Switch |  | 1.001: switch | 1/2/6 | 1/2/106
Bld01.F06 |  | 1F06_1-6GGAL_07.Ctl | Switch |  | 1.001: switch | 1/2/7 | 1/2/107
Bld01.F06 |  | 1F06_1-6GGAL_08.Ctl | Switch |  | 1.001: switch | 1/2/8 | 1/2/108
Bld01.F07 |  | 1F07_1-7GGAL_01.Ctl | Switch |  | 1.001: switch | 1/2/21 | 1/2/121
Bld01.F07 |  | 1F07_1-7GGAL_02.Ctl | Switch |  | 1.001: switch | 1/2/22 | 1/2/122
Bld01.F07 |  | 1F07_1-7GGAL_03.Ctl | Switch |  | 1.001: switch | 1/2/23 | 1/2/123
Bld01.F07 |  | 1F07_1-7GGAL_04.Ctl | Switch |  | 1.001: switch | 1/2/24 | 1/2/124
Bld01.F07 |  | 1F07_1-7GGAL_05.Ctl | Switch |  | 1.001: switch | 1/2/25 | 1/2/125
Bld01.F07 |  | 1F07_1-7GGAL_06.Ctl | Switch |  | 1.001: switch | 1/2/26 | 1/2/126
Bld01.F07 |  | 1F07_1-7GGAL_07.Ctl | Switch |  | 1.001: switch | 1/2/27 | 1/2/127
Bld01.F07 |  | 1F07_1-7GGAL_08.Ctl | Switch |  | 1.001: switch | 1/2/28 | 1/2/128
Bld01.F08 |  | 1F08_1-8AT_01.Ctl | Switch |  | 1.001: switch | 1/2/41 | 1/2/141
Bld01.F08 |  | 1F08_1-8AT_02.Ctl | Switch |  | 1.001: switch | 1/2/42 | 1/2/142
Bld01.F08 |  | 1F08_1-8AT_03.Ctl | Switch |  | 1.001: switch | 1/2/43 | 1/2/143
Bld01.F08 |  | 1F08_1-8AT_04.Ctl | Switch |  | 1.001: switch | 1/2/44 | 1/2/144
Bld01.F08 |  | 1F08_1-8AT_05.Ctl | Switch |  | 1.001: switch | 1/2/45 | 1/2/145
Bld01.F08 |  | 1F08_1-8AT_06.Ctl | Switch |  | 1.001: switch | 1/2/46 | 1/2/146
Bld01.F08 |  | 1F08_1-8AT_07.Ctl | Switch |  | 1.001: switch | 1/2/47 | 1/2/147
Bld01.F08 |  | 1F08_1-8AT_08.Ctl | Switch |  | 1.001: switch | 1/2/48 | 1/2/148
Bld01.F09 |  | 1F09_1-9GGAL_01.Ctl | Switch |  | 1.001: switch | 1/2/61 | 1/2/161
Bld01.F09 |  | 1F09_1-9GGAL_02.Ctl | Switch |  | 1.001: switch | 1/2/62 | 1/2/162
Bld01.F09 |  | 1F09_1-9GGAL_03.Ctl | Switch |  | 1.001: switch | 1/2/63 | 1/2/163
Bld01.F09 |  | 1F09_1-9GGAL_04.Ctl | Switch |  | 1.001: switch | 1/2/64 | 1/2/164
Bld01.F09 |  | 1F09_1-9GGAL_05.Ctl | Switch |  | 1.001: switch | 1/2/65 | 1/2/165
Bld01.F09 |  | 1F09_1-9GGAL_06.Ctl | Switch |  | 1.001: switch | 1/2/66 | 1/2/166
Bld01.F09 |  | 1F09_1-9GGAL_07.Ctl | Switch |  | 1.001: switch | 1/2/67 | 1/2/167
Bld01.F09 |  | 1F09_1-9GGAL_08.Ctl | Switch |  | 1.001: switch | 1/2/68 | 1/2/168
Bld01.F10 |  | 1F10_1-10GGAL_01.Ctl | Switch |  | 1.001: switch | 1/2/81 | 1/2/181
Bld01.F10 |  | 1F10_1-10GGAL_02.Ctl | Switch |  | 1.001: switch | 1/2/82 | 1/2/182
Bld01.F10 |  | 1F10_1-10GGAL_03.Ctl | Switch |  | 1.001: switch | 1/2/83 | 1/2/183
Bld01.F10 |  | 1F10_1-10GGAL_04.Ctl | Switch |  | 1.001: switch | 1/2/84 | 1/2/184
Bld01.F10 |  | 1F10_1-10GGAL_05.Ctl | Switch |  | 1.001: switch | 1/2/85 | 1/2/185
Bld01.F10 |  | 1F10_1-10GGAL_06.Ctl | Switch |  | 1.001: switch | 1/2/86 | 1/2/186
Bld01.F10 |  | 1F10_1-10GGAL_07.Ctl | Switch |  | 1.001: switch | 1/2/87 | 1/2/187
Bld01.F10 |  | 1F10_1-10GGAL_08.Ctl | Switch |  | 1.001: switch | 1/2/88 | 1/2/188
Bld01.F06 |  | 1F06_Scd.En | EnableCtl | [1号楼]定时_F06 | 1.003: enable | 1/2/221
Bld01.F07 |  | 1F07_Scd.En | EnableCtl | [1号楼]定时_F07 | 1.003: enable | 1/2/222
Bld01.F08 |  | 1F08_Scd.En | EnableCtl | [1号楼]定时_F08 | 1.003: enable | 1/2/223
Bld01.F09 |  | 1F09_Scd.En | EnableCtl | [1号楼]定时_F09 | 1.003: enable | 1/2/224
Bld01.F10 |  | 1F10_Scd.En | EnableCtl | [1号楼]定时_F10 | 1.003: enable | 1/2/225
Bld01.F06 |  | 1F06_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F06 | 1.002: boolean | 1/2/231
Bld01.F07 |  | 1F07_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F07 | 1.002: boolean | 1/2/232
Bld01.F08 |  | 1F08_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F08 | 1.002: boolean | 1/2/233
Bld01.F09 |  | 1F09_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F09 | 1.002: boolean | 1/2/234
Bld01.F10 |  | 1F10_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F10 | 1.002: boolean | 1/2/235
Bld01.F06 |  | 1F06_Pb.Lock | EnableCtl | [1号楼]面板锁定_F06 | 1.002: boolean | 1/2/241
Bld01.F07 |  | 1F07_Pb.Lock | EnableCtl | [1号楼]面板锁定_F07 | 1.002: boolean | 1/2/242
Bld01.F08 |  | 1F08_Pb.Lock | EnableCtl | [1号楼]面板锁定_F08 | 1.002: boolean | 1/2/243
Bld01.F09 |  | 1F09_Pb.Lock | EnableCtl | [1号楼]面板锁定_F09 | 1.002: boolean | 1/2/244
Bld01.F10 |  | 1F10_Pb.Lock | EnableCtl | [1号楼]面板锁定_F10 | 1.002: boolean | 1/2/245
Bld01.F11 |  | 1F11_1-11GGAL_01.Ctl | Switch |  | 1.001: switch | 1/3/1 | 1/3/101
Bld01.F11 |  | 1F11_1-11GGAL_02.Ctl | Switch |  | 1.001: switch | 1/3/2 | 1/3/102
Bld01.F11 |  | 1F11_1-11GGAL_03.Ctl | Switch |  | 1.001: switch | 1/3/3 | 1/3/103
Bld01.F11 |  | 1F11_1-11GGAL_04.Ctl | Switch |  | 1.001: switch | 1/3/4 | 1/3/104
Bld01.F11 |  | 1F11_1-11GGAL_05.Ctl | Switch |  | 1.001: switch | 1/3/5 | 1/3/105
Bld01.F11 |  | 1F11_1-11GGAL_06.Ctl | Switch |  | 1.001: switch | 1/3/6 | 1/3/106
Bld01.F11 |  | 1F11_1-11GGAL_07.Ctl | Switch |  | 1.001: switch | 1/3/7 | 1/3/107
Bld01.F11 |  | 1F11_1-11GGAL_08.Ctl | Switch |  | 1.001: switch | 1/3/8 | 1/3/108
Bld01.F12 |  | 1F12_1-12GGAL_01.Ctl | Switch |  | 1.001: switch | 1/3/21 | 1/3/121
Bld01.F12 |  | 1F12_1-12GGAL_02.Ctl | Switch |  | 1.001: switch | 1/3/22 | 1/3/122
Bld01.F12 |  | 1F12_1-12GGAL_03.Ctl | Switch |  | 1.001: switch | 1/3/23 | 1/3/123
Bld01.F12 |  | 1F12_1-12GGAL_04.Ctl | Switch |  | 1.001: switch | 1/3/24 | 1/3/124
Bld01.F12 |  | 1F12_1-12GGAL_05.Ctl | Switch |  | 1.001: switch | 1/3/25 | 1/3/125
Bld01.F12 |  | 1F12_1-12GGAL_06.Ctl | Switch |  | 1.001: switch | 1/3/26 | 1/3/126
Bld01.F12 |  | 1F12_1-12GGAL_07.Ctl | Switch |  | 1.001: switch | 1/3/27 | 1/3/127
Bld01.F12 |  | 1F12_1-12GGAL_08.Ctl | Switch |  | 1.001: switch | 1/3/28 | 1/3/128
Bld01.F13 |  | 1F13_1-13GGAL_01.Ctl | Switch |  | 1.001: switch | 1/3/41 | 1/3/141
Bld01.F13 |  | 1F13_1-13GGAL_02.Ctl | Switch |  | 1.001: switch | 1/3/42 | 1/3/142
Bld01.F13 |  | 1F13_1-13GGAL_03.Ctl | Switch |  | 1.001: switch | 1/3/43 | 1/3/143
Bld01.F13 |  | 1F13_1-13GGAL_04.Ctl | Switch |  | 1.001: switch | 1/3/44 | 1/3/144
Bld01.F13 |  | 1F13_1-13GGAL_05.Ctl | Switch |  | 1.001: switch | 1/3/45 | 1/3/145
Bld01.F13 |  | 1F13_1-13GGAL_06.Ctl | Switch |  | 1.001: switch | 1/3/46 | 1/3/146
Bld01.F13 |  | 1F13_1-13GGAL_07.Ctl | Switch |  | 1.001: switch | 1/3/47 | 1/3/147
Bld01.F13 |  | 1F13_1-13GGAL_08.Ctl | Switch |  | 1.001: switch | 1/3/48 | 1/3/148
Bld01.F14 |  | 1F14_1-14GGAL_01.Ctl | Switch |  | 1.001: switch | 1/3/61 | 1/3/161
Bld01.F14 |  | 1F14_1-14GGAL_02.Ctl | Switch |  | 1.001: switch | 1/3/62 | 1/3/162
Bld01.F14 |  | 1F14_1-14GGAL_03.Ctl | Switch |  | 1.001: switch | 1/3/63 | 1/3/163
Bld01.F14 |  | 1F14_1-14GGAL_04.Ctl | Switch |  | 1.001: switch | 1/3/64 | 1/3/164
Bld01.F14 |  | 1F14_1-14GGAL_05.Ctl | Switch |  | 1.001: switch | 1/3/65 | 1/3/165
Bld01.F14 |  | 1F14_1-14GGAL_06.Ctl | Switch |  | 1.001: switch | 1/3/66 | 1/3/166
Bld01.F14 |  | 1F14_1-14GGAL_07.Ctl | Switch |  | 1.001: switch | 1/3/67 | 1/3/167
Bld01.F14 |  | 1F14_1-14GGAL_08.Ctl | Switch |  | 1.001: switch | 1/3/68 | 1/3/168
Bld01.F15 |  | 1F15_1-15GGAL_01.Ctl | Switch |  | 1.001: switch | 1/3/81 | 1/3/181
Bld01.F15 |  | 1F15_1-15GGAL_02.Ctl | Switch |  | 1.001: switch | 1/3/82 | 1/3/182
Bld01.F15 |  | 1F15_1-15GGAL_03.Ctl | Switch |  | 1.001: switch | 1/3/83 | 1/3/183
Bld01.F15 |  | 1F15_1-15GGAL_04.Ctl | Switch |  | 1.001: switch | 1/3/84 | 1/3/184
Bld01.F15 |  | 1F15_1-15GGAL_05.Ctl | Switch |  | 1.001: switch | 1/3/85 | 1/3/185
Bld01.F15 |  | 1F15_1-15GGAL_06.Ctl | Switch |  | 1.001: switch | 1/3/86 | 1/3/186
Bld01.F15 |  | 1F15_1-15GGAL_07.Ctl | Switch |  | 1.001: switch | 1/3/87 | 1/3/187
Bld01.F15 |  | 1F15_1-15GGAL_08.Ctl | Switch |  | 1.001: switch | 1/3/88 | 1/3/188
Bld01.F11 |  | 1F11_Scd.En | EnableCtl | [1号楼]定时_F11 | 1.003: enable | 1/3/221
Bld01.F12 |  | 1F12_Scd.En | EnableCtl | [1号楼]定时_F12 | 1.003: enable | 1/3/222
Bld01.F13 |  | 1F13_Scd.En | EnableCtl | [1号楼]定时_F13 | 1.003: enable | 1/3/223
Bld01.F14 |  | 1F14_Scd.En | EnableCtl | [1号楼]定时_F14 | 1.003: enable | 1/3/224
Bld01.F15 |  | 1F15_Scd.En | EnableCtl | [1号楼]定时_F15 | 1.003: enable | 1/3/225
Bld01.F11 |  | 1F11_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F11 | 1.002: boolean | 1/3/231
Bld01.F12 |  | 1F12_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F12 | 1.002: boolean | 1/3/232
Bld01.F13 |  | 1F13_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F13 | 1.002: boolean | 1/3/233
Bld01.F14 |  | 1F14_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F14 | 1.002: boolean | 1/3/234
Bld01.F15 |  | 1F15_Actr.Lock | EnableCtl | [1号楼]执行器锁定_F15 | 1.002: boolean | 1/3/235
Bld01.F11 |  | 1F11_Pb.Lock | EnableCtl | [1号楼]面板锁定_F11 | 1.002: boolean | 1/3/241
Bld01.F12 |  | 1F12_Pb.Lock | EnableCtl | [1号楼]面板锁定_F12 | 1.002: boolean | 1/3/242
Bld01.F13 |  | 1F13_Pb.Lock | EnableCtl | [1号楼]面板锁定_F13 | 1.002: boolean | 1/3/243
Bld01.F14 |  | 1F14_Pb.Lock | EnableCtl | [1号楼]面板锁定_F14 | 1.002: boolean | 1/3/244
Bld01.F15 |  | 1F15_Pb.Lock | EnableCtl | [1号楼]面板锁定_F15 | 1.002: boolean | 1/3/245
Bld01.B02 |  | 1B02_5-B2AL_01.Ctl | Switch |  | 1.001: switch | 1/7/1 | 1/7/101
Bld01.B02 |  | 1B02_5-B2AL_02.Ctl | Switch |  | 1.001: switch | 1/7/2 | 1/7/102
Bld01.B02 |  | 1B02_5-B2AL_03.Ctl | Switch |  | 1.001: switch | 1/7/3 | 1/7/103
Bld01.B02 |  | 1B02_5-B2AL_04.Ctl | Switch |  | 1.001: switch | 1/7/4 | 1/7/104
Bld01.B02 |  | 1B02_5-B2AL_05.Ctl | Switch |  | 1.001: switch | 1/7/5 | 1/7/105
Bld01.B02 |  | 1B02_5-B2AL_06.Ctl | Switch |  | 1.001: switch | 1/7/6 | 1/7/106
Bld01.B02 |  | 1B02_5-B2AL_07.Ctl | Switch |  | 1.001: switch | 1/7/7 | 1/7/107
Bld01.B02 |  | 1B02_5-B2AL_08.Ctl | Switch |  | 1.001: switch | 1/7/8 | 1/7/108
Bld01.B02 |  | 1B02_1-B2GGAL_01.Ctl | Switch |  | 1.001: switch | 1/7/21 | 1/7/121
Bld01.B02 |  | 1B02_1-B2GGAL_02.Ctl | Switch |  | 1.001: switch | 1/7/22 | 1/7/122
Bld01.B02 |  | 1B02_1-B2GGAL_03.Ctl | Switch |  | 1.001: switch | 1/7/23 | 1/7/123
Bld01.B02 |  | 1B02_1-B2GGAL_04.Ctl | Switch |  | 1.001: switch | 1/7/24 | 1/7/124
Bld01.B02 |  | 1B02_1-B2GGAL_05.Ctl | Switch |  | 1.001: switch | 1/7/25 | 1/7/125
Bld01.B02 |  | 1B02_1-B2GGAL_06.Ctl | Switch |  | 1.001: switch | 1/7/26 | 1/7/126
Bld01.B02 |  | 1B02_1-B2GGAL_07.Ctl | Switch |  | 1.001: switch | 1/7/27 | 1/7/127
Bld01.B02 |  | 1B02_1-B2GGAL_08.Ctl | Switch |  | 1.001: switch | 1/7/28 | 1/7/128
Bld01.B01 |  | 1B01_1-B1GGAL_01.Ctl | Switch |  | 1.001: switch | 1/7/41 | 1/7/141
Bld01.B01 |  | 1B01_1-B1GGAL_02.Ctl | Switch |  | 1.001: switch | 1/7/42 | 1/7/142
Bld01.B01 |  | 1B01_1-B1GGAL_03.Ctl | Switch |  | 1.001: switch | 1/7/43 | 1/7/143
Bld01.B01 |  | 1B01_1-B1GGAL_04.Ctl | Switch |  | 1.001: switch | 1/7/44 | 1/7/144
Bld01.B01 |  | 1B01_1-B1GGAL_05.Ctl | Switch |  | 1.001: switch | 1/7/45 | 1/7/145
Bld01.B01 |  | 1B01_1-B1GGAL_06.Ctl | Switch |  | 1.001: switch | 1/7/46 | 1/7/146
Bld01.B01 |  | 1B01_1-B1GGAL_07.Ctl | Switch |  | 1.001: switch | 1/7/47 | 1/7/147
Bld01.B01 |  | 1B01_1-B1GGAL_08.Ctl | Switch |  | 1.001: switch | 1/7/48 | 1/7/148
Bld01.B01 |  | 1B01_1-B1GGAL_09.Ctl | Switch |  | 1.001: switch | 1/7/49 | 1/7/149
Bld01.B01 |  | 1B01_1-B1GGAL_10.Ctl | Switch |  | 1.001: switch | 1/7/50 | 1/7/150
Bld01.B01 |  | 1B01_1-B1GGAL_11.Ctl | Switch |  | 1.001: switch | 1/7/51 | 1/7/151
Bld01.B01 |  | 1B01_1-B1GGAL_12.Ctl | Switch |  | 1.001: switch | 1/7/52 | 1/7/152
Bld01.B01 |  | 1B01_Scd.En | EnableCtl | [1号楼]定时_B01 | 1.003: enable | 1/7/221
Bld01.B02 |  | 1B02_Scd.En | EnableCtl | [1号楼]定时_B02 | 1.003: enable | 1/7/222
Bld01.B01 |  | 1B01_1-B1GGAL_Scd.En | EnableCtl | [1号楼]定时_B01_1-B1GGAL | 1.003: enable | 1/7/227
Bld01.B02 |  | 1B02_1-B2GGAL_Scd.En | EnableCtl | [1号楼]定时_B02_1-B2GGAL | 1.003: enable | 1/7/228
Bld01.B02 |  | 1B02_5-B2AL_Scd.En | EnableCtl | [1号楼]定时_B02_5-B2AL | 1.003: enable | 1/7/229
Bld01.B01 |  | 1B01_Actr.Lock | EnableCtl | [1号楼]执行器锁定_B01 | 1.002: boolean | 1/7/231
Bld01.B02 |  | 1B02_Actr.Lock | EnableCtl | [1号楼]执行器锁定_B02 | 1.002: boolean | 1/7/232
Bld01.B01 |  | 1B01_1-B1GGAL_Actr.Lock | EnableCtl | [1号楼]执行器锁定_B01_1-B1GGAL | 1.002: boolean | 1/7/237
Bld01.B02 |  | 1B02_1-B2GGAL_Actr.Lock | EnableCtl | [1号楼]执行器锁定_B02_1-B2GGAL | 1.002: boolean | 1/7/238
Bld01.B02 |  | 1B02_5-B2AL_Actr.Lock | EnableCtl | [1号楼]执行器锁定_B02_5-B2AL | 1.002: boolean | 1/7/239
Bld01.B01 |  | 1B01_Pb.Lock | EnableCtl | [1号楼]面板锁定_B01 | 1.002: boolean | 1/7/241
Bld01.B02 |  | 1B02_Pb.Lock | EnableCtl | [1号楼]面板锁定_B02 | 1.002: boolean | 1/7/242
Bld01.B01 |  | 1B01_1-B1GGAL_Pb.Lock | EnableCtl | [1号楼]面板锁定_B01_1-B1GGAL | 1.002: boolean | 1/7/247
Bld01.B02 |  | 1B02_1-B2GGAL_Pb.Lock | EnableCtl | [1号楼]面板锁定_B02_1-B2GGAL | 1.002: boolean | 1/7/248
Bld01.B02 |  | 1B02_5-B2AL_Pb.Lock | EnableCtl | [1号楼]面板锁定_B02_5-B2AL | 1.002: boolean | 1/7/249
Bld03 |  | 3_Scd.En | EnableCtl | [3号楼]定时 | 1.003: enable | 3/0/220
Bld03 |  | 3_Actr.Lock | EnableCtl | [3号楼]执行器锁定 | 1.002: boolean | 3/0/230
Bld03 |  | 3_Pb.Lock | EnableCtl | [3号楼]面板锁定 | 1.002: boolean | 3/0/240
Bld03.F01 |  | 3F01_3-1AT_01.Ctl | Switch |  | 1.001: switch | 3/1/1 | 3/1/101
Bld03.F01 |  | 3F01_3-1AT_02.Ctl | Switch |  | 1.001: switch | 3/1/2 | 3/1/102
Bld03.F01 |  | 3F01_3-1AT_03.Ctl | Switch |  | 1.001: switch | 3/1/3 | 3/1/103
Bld03.F01 |  | 3F01_3-1AT_04.Ctl | Switch |  | 1.001: switch | 3/1/4 | 3/1/104
Bld03.F01 |  | 3F01_3-1AT_05.Ctl | Switch |  | 1.001: switch | 3/1/5 | 3/1/105
Bld03.F01 |  | 3F01_3-1AT_06.Ctl | Switch |  | 1.001: switch | 3/1/6 | 3/1/106
Bld03.F01 |  | 3F01_3-1AT_07.Ctl | Switch |  | 1.001: switch | 3/1/7 | 3/1/107
Bld03.F01 |  | 3F01_3-1AT_08.Ctl | Switch |  | 1.001: switch | 3/1/8 | 3/1/108
Bld03.F01 |  | 3F01_3-1AT_09.Ctl | Switch |  | 1.001: switch | 3/1/9 | 3/1/109
Bld03.F01 |  | 3F01_3-1AT_10.Ctl | Switch |  | 1.001: switch | 3/1/10 | 3/1/110
Bld03.F01 |  | 3F01_3-1AT_11.Ctl | Switch |  | 1.001: switch | 3/1/11 | 3/1/111
Bld03.F01 |  | 3F01_3-1AT_12.Ctl | Switch |  | 1.001: switch | 3/1/12 | 3/1/112
Bld03.F01 |  | 3F01_Scd.En | EnableCtl | [3号楼]定时_F01 | 1.003: enable | 3/1/220
Bld03.F01 |  | 3F01_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F01 | 1.002: boolean | 3/1/230
Bld03.F01 |  | 3F01_Pb.Lock | EnableCtl | [3号楼]面板锁定_F01 | 1.002: boolean | 3/1/240
Bld03.F02 |  | 3F02_3-2GGAL_01.Ctl | Switch |  | 1.001: switch | 3/2/1 | 3/2/101
Bld03.F02 |  | 3F02_3-2GGAL_02.Ctl | Switch |  | 1.001: switch | 3/2/2 | 3/2/102
Bld03.F02 |  | 3F02_3-2GGAL_03.Ctl | Switch |  | 1.001: switch | 3/2/3 | 3/2/103
Bld03.F02 |  | 3F02_3-2GGAL_04.Ctl | Switch |  | 1.001: switch | 3/2/4 | 3/2/104
Bld03.F02 |  | 3F02_3-2GGAL_05.Ctl | Switch |  | 1.001: switch | 3/2/5 | 3/2/105
Bld03.F02 |  | 3F02_3-2GGAL_06.Ctl | Switch |  | 1.001: switch | 3/2/6 | 3/2/106
Bld03.F02 |  | 3F02_3-2GGAL_07.Ctl | Switch |  | 1.001: switch | 3/2/7 | 3/2/107
Bld03.F02 |  | 3F02_3-2GGAL_08.Ctl | Switch |  | 1.001: switch | 3/2/8 | 3/2/108
Bld03.F02 |  | 3F02_Scd.En | EnableCtl | [3号楼]定时_F02 | 1.003: enable | 3/2/220
Bld03.F02 |  | 3F02_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F02 | 1.002: boolean | 3/2/230
Bld03.F02 |  | 3F02_Pb.Lock | EnableCtl | [3号楼]面板锁定_F02 | 1.002: boolean | 3/2/240
Bld03.F03 |  | 3F03_3-3GGAL_01.Ctl | Switch |  | 1.001: switch | 3/3/1 | 3/3/101
Bld03.F03 |  | 3F03_3-3GGAL_02.Ctl | Switch |  | 1.001: switch | 3/3/2 | 3/3/102
Bld03.F03 |  | 3F03_3-3GGAL_03.Ctl | Switch |  | 1.001: switch | 3/3/3 | 3/3/103
Bld03.F03 |  | 3F03_3-3GGAL_04.Ctl | Switch |  | 1.001: switch | 3/3/4 | 3/3/104
Bld03.F03 |  | 3F03_3-3GGAL_05.Ctl | Switch |  | 1.001: switch | 3/3/5 | 3/3/105
Bld03.F03 |  | 3F03_3-3GGAL_06.Ctl | Switch |  | 1.001: switch | 3/3/6 | 3/3/106
Bld03.F03 |  | 3F03_3-3GGAL_07.Ctl | Switch |  | 1.001: switch | 3/3/7 | 3/3/107
Bld03.F03 |  | 3F03_3-3GGAL_08.Ctl | Switch |  | 1.001: switch | 3/3/8 | 3/3/108
Bld03.F03 |  | 3F03_4-3AT_01.Ctl | Switch |  | 1.001: switch | 3/3/21 | 3/3/121
Bld03.F03 |  | 3F03_4-3AT_02.Ctl | Switch |  | 1.001: switch | 3/3/22 | 3/3/122
Bld03.F03 |  | 3F03_4-3AT_03.Ctl | Switch |  | 1.001: switch | 3/3/23 | 3/3/123
Bld03.F03 |  | 3F03_4-3AT_04.Ctl | Switch |  | 1.001: switch | 3/3/24 | 3/3/124
Bld03.F03 |  | 3F03_4-3AT_05.Ctl | Switch |  | 1.001: switch | 3/3/25 | 3/3/125
Bld03.F03 |  | 3F03_4-3AT_06.Ctl | Switch |  | 1.001: switch | 3/3/26 | 3/3/126
Bld03.F03 |  | 3F03_4-3AT_07.Ctl | Switch |  | 1.001: switch | 3/3/27 | 3/3/127
Bld03.F03 |  | 3F03_4-3AT_08.Ctl | Switch |  | 1.001: switch | 3/3/28 | 3/3/128
Bld03.F03 |  | 3F03_Scd.En | EnableCtl | [3号楼]定时_F03 | 1.003: enable | 3/3/220
Bld03.F03 |  | 3F03_3-3GGAL_Scd.En | EnableCtl | [3号楼]定时_F03_3-3GGAL | 1.003: enable | 3/3/221
Bld03.F03 |  | 3F03_4-3AT_Scd.En | EnableCtl | [3号楼]定时_F03_4-3AT | 1.003: enable | 3/3/222
Bld03.F03 |  | 3F03_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F03 | 1.002: boolean | 3/3/230
Bld03.F03 |  | 3F03_3-3GGAL_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F03_3-3GGAL | 1.002: boolean | 3/3/231
Bld03.F03 |  | 3F03_4-3AT_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F03_4-3AT | 1.002: boolean | 3/3/232
Bld03.F03 |  | 3F03_Pb.Lock | EnableCtl | [3号楼]面板锁定_F03 | 1.002: boolean | 3/3/240
Bld03.F03 |  | 3F03_3-3GGAL_Pb.Lock | EnableCtl | [3号楼]面板锁定_F03_3-3GGAL | 1.002: boolean | 3/3/241
Bld03.F03 |  | 3F03_4-3AT_Pb.Lock | EnableCtl | [3号楼]面板锁定_F03_4-3AT | 1.002: boolean | 3/3/242
Bld03.F04 |  | 3F04_3-4GGAL_01.Ctl | Switch |  | 1.001: switch | 3/4/1 | 3/4/101
Bld03.F04 |  | 3F04_3-4GGAL_02.Ctl | Switch |  | 1.001: switch | 3/4/2 | 3/4/102
Bld03.F04 |  | 3F04_3-4GGAL_03.Ctl | Switch |  | 1.001: switch | 3/4/3 | 3/4/103
Bld03.F04 |  | 3F04_3-4GGAL_04.Ctl | Switch |  | 1.001: switch | 3/4/4 | 3/4/104
Bld03.F04 |  | 3F04_3-4GGAL_05.Ctl | Switch |  | 1.001: switch | 3/4/5 | 3/4/105
Bld03.F04 |  | 3F04_3-4GGAL_06.Ctl | Switch |  | 1.001: switch | 3/4/6 | 3/4/106
Bld03.F04 |  | 3F04_3-4GGAL_07.Ctl | Switch |  | 1.001: switch | 3/4/7 | 3/4/107
Bld03.F04 |  | 3F04_3-4GGAL_08.Ctl | Switch |  | 1.001: switch | 3/4/8 | 3/4/108
Bld03.F04 |  | 3F04_4-4GGAL_01.Ctl | Switch |  | 1.001: switch | 3/4/21 | 3/4/121
Bld03.F04 |  | 3F04_4-4GGAL_02.Ctl | Switch |  | 1.001: switch | 3/4/22 | 3/4/122
Bld03.F04 |  | 3F04_4-4GGAL_03.Ctl | Switch |  | 1.001: switch | 3/4/23 | 3/4/123
Bld03.F04 |  | 3F04_4-4GGAL_04.Ctl | Switch |  | 1.001: switch | 3/4/24 | 3/4/124
Bld03.F04 |  | 3F04_4-4GGAL_05.Ctl | Switch |  | 1.001: switch | 3/4/25 | 3/4/125
Bld03.F04 |  | 3F04_4-4GGAL_06.Ctl | Switch |  | 1.001: switch | 3/4/26 | 3/4/126
Bld03.F04 |  | 3F04_4-4GGAL_07.Ctl | Switch |  | 1.001: switch | 3/4/27 | 3/4/127
Bld03.F04 |  | 3F04_4-4GGAL_08.Ctl | Switch |  | 1.001: switch | 3/4/28 | 3/4/128
Bld03.F04 |  | 3F04_Scd.En | EnableCtl | [3号楼]定时_F04 | 1.003: enable | 3/4/220
Bld03.F04 |  | 3F04_3-4GGAL_Scd.En | EnableCtl | [3号楼]定时_F04_3-4GGAL | 1.003: enable | 3/4/221
Bld03.F04 |  | 3F04_4-4GGAL_Scd.En | EnableCtl | [3号楼]定时_F04_4-4GGAL | 1.003: enable | 3/4/222
Bld03.F04 |  | 3F04_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F04 | 1.002: boolean | 3/4/230
Bld03.F04 |  | 3F04_3-4GGAL_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F04_3-4GGAL | 1.002: boolean | 3/4/231
Bld03.F04 |  | 3F04_4-4GGAL_Actr.Lock | EnableCtl | [3号楼]执行器锁定_F04_4-4GGAL | 1.002: boolean | 3/4/232
Bld03.F04 |  | 3F04_Pb.Lock | EnableCtl | [3号楼]面板锁定_F04 | 1.002: boolean | 3/4/240
Bld03.F04 |  | 3F04_3-4GGAL_Pb.Lock | EnableCtl | [3号楼]面板锁定_F04_3-4GGAL | 1.002: boolean | 3/4/241
Bld03.F04 |  | 3F04_4-4GGAL_Pb.Lock | EnableCtl | [3号楼]面板锁定_F04_4-4GGAL | 1.002: boolean | 3/4/242
Bld06.F01 |  | 6F01_1-6AL_01.Ctl | Switch |  | 1.001: switch | 6/1/1 | 6/1/101
Bld06.F01 |  | 6F01_1-6AL_02.Ctl | Switch |  | 1.001: switch | 6/1/2 | 6/1/102
Bld06.F01 |  | 6F01_1-6AL_03.Ctl | Switch |  | 1.001: switch | 6/1/3 | 6/1/103
Bld06.F01 |  | 6F01_1-6AL_04.Ctl | Switch |  | 1.001: switch | 6/1/4 | 6/1/104
Bld06.F01 |  | 6F01_1-6AL_05.Ctl | Switch |  | 1.001: switch | 6/1/5 | 6/1/105
Bld06.F01 |  | 6F01_1-6AL_06.Ctl | Switch |  | 1.001: switch | 6/1/6 | 6/1/106
Bld06.F01 |  | 6F01_1-6AL_07.Ctl | Switch |  | 1.001: switch | 6/1/7 | 6/1/107
Bld06.F01 |  | 6F01_1-6AL_08.Ctl | Switch |  | 1.001: switch | 6/1/8 | 6/1/108
Bld06.F01 |  | 6F01_Scd.En | EnableCtl | [6号楼]定时_F01 | 1.003: enable | 6/1/220
Bld06.F01 |  | 6F01_Actr.Lock | EnableCtl | [6号楼]执行器锁定_F01 | 1.002: boolean | 6/1/230
Bld06.F01 |  | 6F01_Pb.Lock | EnableCtl | [6号楼]面板锁定_F01 | 1.002: boolean | 6/1/240
Note on B2: 对象支持对应多个接口但是不推荐，多个接口之间用英文逗号分隔。
Note on C2: 对象编号不允许重复

## Scenes
AreaCode | InterfaceCode | SceneCode | SceneName | GroupAddress | SceneValues
区域编号 | 接口编号 | 场景编号 | 场景名称 | 组地址 | 场景值
Garage |  | gB01_Scn.Ctl | [地下车库]场景_全部 | 0/0/210 | 0=全关,1=全开
Garage |  | gB01_B1-6AT1_Scn.Ctl | [地下车库]场景_B1-6AT1 | 0/1/211 | 0=全关,1=全开
Garage |  | gB01_B1-6AT2_Scn.Ctl | [地下车库]场景_B1-6AT2 | 0/1/212 | 0=全关,1=全开
Garage |  | gB01_B1-8AT_Scn.Ctl | [地下车库]场景_B1-8AT | 0/1/213 | 0=全关,1=全开
Garage |  | gB01_B1-9AL_Scn.Ctl | [地下车库]场景_B1-9AL | 0/1/214 | 0=全关,1=全开
Garage |  | gB01_B1-10AT_Scn.Ctl | [地下车库]场景_B1-10AT | 0/2/211 | 0=全关,1=全开
Garage |  | gB01_B1-11AT1_Scn.Ctl | [地下车库]场景_B1-11AT1 | 0/2/212 | 0=全关,1=全开
Garage |  | gB01_B1-11AT2_Scn.Ctl | [地下车库]场景_B1-11AT2 | 0/2/213 | 0=全关,1=全开
Garage |  | gB01_B1-16AT_Scn.Ctl | [地下车库]场景_B1-16AT | 0/2/214 | 0=全关,1=全开
Garage |  | gB01_B1-18AT_Scn.Ctl | [地下车库]场景_B1-18AT | 0/3/211 | 0=全关,1=全开
Garage |  | gB01_B1-19AT_Scn.Ctl | [地下车库]场景_B1-19AT | 0/3/212 | 0=全关,1=全开
Garage |  | gB01_B1-22AT1_Scn.Ctl | [地下车库]场景_B1-22AT1 | 0/3/213 | 0=全关,1=全开
Garage |  | gB01_B1-22AT2_Scn.Ctl | [地下车库]场景_B1-22AT2 | 0/3/214 | 0=全关,1=全开
Bld1 |  | 1_Scn.Ctl | [1号楼]场景_全部 | 1/0/210 | 0=全关,1=全开
Bld01.F01 |  | 1F01_Scn.Ctl | [1号楼]场景_F01 | 1/1/211 | 0=全关,1=全开
Bld01.F02 |  | 1F02_Scn.Ctl | [1号楼]场景_F02 | 1/1/212 | 0=全关,1=全开
Bld01.F03 |  | 1F03_Scn.Ctl | [1号楼]场景_F03 | 1/1/213 | 0=全关,1=全开
Bld01.F04 |  | 1F04_Scn.Ctl | [1号楼]场景_F04 | 1/1/214 | 0=全关,1=全开
Bld01.F05 |  | 1F05_Scn.Ctl | [1号楼]场景_F05 | 1/1/215 | 0=全关,1=全开
Bld01.F06 |  | 1F06_Scn.Ctl | [1号楼]场景_F06 | 1/2/211 | 0=全关,1=全开
Bld01.F07 |  | 1F07_Scn.Ctl | [1号楼]场景_F07 | 1/2/212 | 0=全关,1=全开
Bld01.F08 |  | 1F08_Scn.Ctl | [1号楼]场景_F08 | 1/2/213 | 0=全关,1=全开
Bld01.F09 |  | 1F09_Scn.Ctl | [1号楼]场景_F09 | 1/2/214 | 0=全关,1=全开
Bld01.F10 |  | 1F10_Scn.Ctl | [1号楼]场景_F10 | 1/2/215 | 0=全关,1=全开
Bld01.F11 |  | 1F11_Scn.Ctl | [1号楼]场景_F11 | 1/3/211 | 0=全关,1=全开
Bld01.F12 |  | 1F12_Scn.Ctl | [1号楼]场景_F12 | 1/3/212 | 0=全关,1=全开
Bld01.F13 |  | 1F13_Scn.Ctl | [1号楼]场景_F13 | 1/3/213 | 0=全关,1=全开
Bld01.F14 |  | 1F14_Scn.Ctl | [1号楼]场景_F14 | 1/3/214 | 0=全关,1=全开
Bld01.F15 |  | 1F15_Scn.Ctl | [1号楼]场景_F15 | 1/3/215 | 0=全关,1=全开
Bld01.B01 |  | 1B01_Scn.Ctl | [1号楼]场景_B01 | 1/7/211 | 0=全关,1=全开
Bld01.B02 |  | 1B02_Scn.Ctl | [1号楼]场景_B02 | 1/7/212 | 0=全关,1=全开
Bld01.B01 |  | 1B01_1-B1GGAL_Scn.Ctl | [1号楼]场景_B01_1-B1GGAL | 1/7/217 | 0=全关,1=全开
Bld01.B02 |  | 1B02_1-B2GGAL_Scn.Ctl | [1号楼]场景_B02_1-B2GGAL | 1/7/218 | 0=全关,1=全开
Bld01.B02 |  | 1B02_5-B2AL_Scn.Ctl | [1号楼]场景_B02_5-B2AL | 1/7/219 | 0=全关,1=全开
Bld03.F01 |  | 3_Scn.Ctl | [3号楼]场景 | 3/0/210 | 0=全关,1=全开
Bld03.F01 |  | 3F01_Scn.Ctl | [3号楼]场景_F01 | 3/1/210 | 0=全关,1=全开
Bld03.F02 |  | 3F02_Scn.Ctl | [3号楼]场景_F02 | 3/2/210 | 0=全关,1=全开
Bld03.F03 |  | 3F03_Scn.Ctl | [3号楼]场景_F03 | 3/3/210 | 0=全关,1=全开
Bld03.F03 |  | 3F03_3-3GGAL_Scn.Ctl | [3号楼]场景_F03_3-3GGAL | 3/3/211 | 0=全关,1=全开
Bld03.F03 |  | 3F03_4-3AT_Scn.Ctl | [3号楼]场景_F03_4-3AT | 3/3/212 | 0=全关,1=全开
Bld03.F04 |  | 3F04_Scn.Ctl | [3号楼]场景_F04 | 3/4/210 | 0=全关,1=全开
Bld03.F04 |  | 3F04_3-4GGAL_Scn.Ctl | [3号楼]场景_F04_3-4GGAL | 3/4/211 | 0=全关,1=全开
Bld03.F04 |  | 3F04_4-4GGAL_Scn.Ctl | [3号楼]场景_F04_4-4GGAL | 3/4/212 | 0=全关,1=全开
Bld06.F01 |  | 6F01_Scn.Ctl | [6号楼]场景_F01 | 6/1/210 | 0=全关,1=全开
Note on B2: 场景支持对应多个接口，多个接口之间用英文逗号分隔。
Note on C2: 场景编号不允许重复
Note on E2: 场景可以有多个组地址，组地址之间用逗号分隔
Note on F2: [场景地址]=[场景名称] 多个场景之间用英文逗号分隔。

## Devices
AreaCode | InterfaceCode | DeviceCode | DeviceName | DeviceModel | IndividualAddress
区域编号 | 接口编号 | 设备编号 | 设备名称 | 设备型号 | 设备地址
Bld01.B02 |  | 1-B2GGAL | KNX网关 | MTN6500-0103 | 1.1.0
Bld01.B02 |  | 1-B2GGAL | 8路开关模块 | MTN6705-0008 | 1.1.221
Bld01.B02 |  | 1-B2GGAL | 6键面板 | C2E616301 | 1.1.229
Bld01.B01 |  | 1-B1GGAL | 12路开关模块 | MTN6700-0312 | 1.1.211
Bld01.B01 |  | 1-B1GGAL | 6键面板 | C2E616301 | 1.1.219
Bld01.F01 |  | 1-1AT | 12路开关模块 | MTN6700-0312 | 1.1.11
Bld01.F01 |  | 1-1AT | 6键面板 | C2E616301 | 1.1.19
Bld01.F02 |  | 1-2GGAL | 8路开关模块 | MTN6705-0008 | 1.1.21
Bld01.F02 |  | 1-2GGAL | 6键面板 | C2E616301 | 1.1.29
Bld01.F03 |  | 1-3GGAL | 8路开关模块 | MTN6705-0008 | 1.1.31
Bld01.F03 |  | 1-3GGAL | 6键面板 | C2E616301 | 1.1.39
Bld01.F04 |  | 1-4GGAL | 8路开关模块 | MTN6705-0008 | 1.1.41
Bld01.F04 |  | 1-4GGAL | 6键面板 | C2E616301 | 1.1.49
Bld01.F05 |  | 1-5GGAL | 8路开关模块 | MTN6705-0008 | 1.1.51
Bld01.F05 |  | 1-5GGAL | 6键面板 | C2E616301 | 1.1.59
Bld01.F06 |  | 1-6GGAL | 8路开关模块 | MTN6705-0008 | 1.1.61
Bld01.F06 |  | 1-6GGAL | 6键面板 | C2E616301 | 1.1.69
Bld01.F07 |  | 1-7GGAL | 8路开关模块 | MTN6705-0008 | 1.1.71
Bld01.F07 |  | 1-7GGAL | 6键面板 | C2E616301 | 1.1.79
Bld01.F08 |  | 1-8AT | 8路开关模块 | MTN6705-0008 | 1.1.81
Bld01.F08 |  | 1-8AT | 6键面板 | C2E616301 | 1.1.89
Bld01.F09 |  | 1-9GGAL | 8路开关模块 | MTN6705-0008 | 1.1.91
Bld01.F09 |  | 1-9GGAL | 6键面板 | C2E616301 | 1.1.99
Bld01.F10 |  | 1-10GGAL | 8路开关模块 | MTN6705-0008 | 1.1.101
Bld01.F10 |  | 1-10GGAL | 6键面板 | C2E616301 | 1.1.109
Bld01.F11 |  | 1-11GGAL | 8路开关模块 | MTN6705-0008 | 1.1.111
Bld01.F11 |  | 1-11GGAL | 6键面板 | C2E616301 | 1.1.119
Bld01.F12 |  | 1-12GGAL | 8路开关模块 | MTN6705-0008 | 1.1.121
Bld01.F12 |  | 1-12GGAL | 6键面板 | C2E616301 | 1.1.129
Bld01.F13 |  | 1-13GGAL | 8路开关模块 | MTN6705-0008 | 1.1.131
Bld01.F13 |  | 1-13GGAL | 6键面板 | C2E616301 | 1.1.139
Bld01.F14 |  | 1-14GGAL | 8路开关模块 | MTN6705-0008 | 1.1.141
Bld01.F14 |  | 1-14GGAL | 6键面板 | C2E616301 | 1.1.149
Bld01.F15 |  | 1-15GGAL | 8路开关模块 | MTN6705-0008 | 1.1.151
Bld01.F15 |  | 1-15GGAL | 6键面板 | C2E616301 | 1.1.159
Bld03.F01 |  | 3-1AT | 12路开关模块 | MTN6700-0312 | 1.3.11
Bld03.F01 |  | 3-1AT | 6键面板 | C2E616301 | 1.3.19
Bld03.F02 |  | 3-2GGAL | 8路开关模块 | MTN6705-0008 | 1.3.21
Bld03.F02 |  | 3-2GGAL | 6键面板 | C2E616301 | 1.3.29
Bld03.F03 |  | 3-3GGAL | 8路开关模块 | MTN6705-0008 | 1.3.31
Bld03.F03 |  | 3-3GGAL | 6键面板 | C2E616301 | 1.3.39
Bld03.F03 |  | 4-3AT | 8路开关模块 | MTN6705-0008 | 1.3.131
Bld03.F03 |  | 4-3AT | 6键面板 | C2E616301 | 1.3.139
Bld03.F04 |  | 3-4GGAL | KNX网关 | MTN6500-0103 | 1.3.0
Bld03.F04 |  | 3-4GGAL | 8路开关模块 | MTN6705-0008 | 1.3.41
Bld03.F04 |  | 3-4GGAL | 6键面板 | C2E616301 | 1.3.49
Bld03.F04 |  | 4-4GGAL | 8路开关模块 | MTN6705-0008 | 1.3.141
Bld03.F04 |  | 4-4GGAL | 6键面板 | C2E616301 | 1.3.149
Bld06.F01 |  | 1-6AL | 8路开关模块 | MTN6705-0008 | 1.6.11
Bld06.F01 |  | 1-6AL | 6键面板 | C2E616301 | 1.6.19
Garage |  | B1-6AT1 | 8路开关模块 | MTN6705-0008 | 1.6.61
Garage |  | B1-6AT1 | 6键面板 | C2E616301 | 1.6.69
Garage |  | B1-6AT2 | 12路开关模块 | MTN6700-0312 | 1.6.62
Garage |  | B1-6AT2 | 6键面板 | C2E616301 | 1.6.68
Garage |  | B1-8AT | 8路开关模块 | MTN6705-0008 | 1.6.81
Garage |  | B1-8AT | 6键面板 | C2E616301 | 1.6.89
Garage |  | B1-9AL | 8路开关模块 | MTN6705-0008 | 1.6.91
Garage |  | B1-9AT | 6键面板 | C2E616301 | 1.6.99
Garage |  | B1-10AT | 8路开关模块 | MTN6705-0008 | 1.6.101
Garage |  | B1-10AT | 6键面板 | C2E616301 | 1.6.109
Garage |  | B1-11AT1 | 8路开关模块 | MTN6705-0008 | 1.6.111
Garage |  | B1-11AT1 | 6键面板 | C2E616301 | 1.6.119
Garage |  | B1-11AT2 | 8路开关模块 | MTN6705-0008 | 1.6.112
Garage |  | B1-11AT2 | 6键面板 | C2E616301 | 1.6.118
Garage |  | B1-16AT | 8路开关模块 | MTN6705-0008 | 1.6.161
Garage |  | B1-16AT | 6键面板 | C2E616301 | 1.6.169
Garage |  | B1-18AT | 8路开关模块 | MTN6705-0008 | 1.6.162
Garage |  | B1-18AT | 6键面板 | C2E616301 | 1.6.168
Garage |  | B1-19AT | KNX网关 | MTN6500-0103 | 1.6.0
Garage |  | B1-19AT | 8路开关模块 | MTN6705-0008 | 1.6.191
Garage |  | B1-19AT | 6键面板 | C2E616301 | 1.6.199
Garage |  | B1-22AT1 | 8路开关模块 | MTN6705-0008 | 1.6.221
Garage |  | B1-22AT1 | 6键面板 | C2E616301 | 1.6.229
Garage |  | B1-22AT2 | 8路开关模块 | MTN6705-0008 | 1.6.222
Garage |  | B1-22AT2 | 6键面板 | C2E616301 | 1.6.228
Note on B2: 设备所在接口的编号。

## Schedules
ScheduleCode | ScheduleName | TargetType | TargetCode | ScheduleEvents | Enable
定时编号 | 定时名称 | 目标对象类型 | 目标对象编号 | 定时事件 | 启用

## Links
LinkName | LinkUrl | Account | Password
链接名称 | 链接地址 | 账号名 | 密码
逻辑控制器 | http://user:User@123@192.168.4.244/scada-vis/schedulers | Admin | Admin@123

## Index_DPT (hidden)
DatapointType
数据点类型
1.xxx: 1-bit
1.001: switch
1.002: boolean
1.003: enable
1.004: ramp
1.005: alarm
1.006: binary value
1.007: step
1.008: up/down
1.009: open/close
1.010: start/stop
1.011: state
1.012: invert
1.013: dim send style
1.014: input source
1.015: reset
1.016: acknowledge
1.017: trigger
1.018: occupancy
1.019: window/door
1.021: logical function
1.022: scene
1.023: shutter/blinds mode
1.024: day/night
1.100: cooling/heating
2.xxx: 1-bit controlled
2.001: switch control
2.002: boolean control
2.003: enable control
2.004: ramp control
2.005: alarm control
2.006: binary value control
2.007: step control
2.008: direction control 1
2.009: direction control 2
2.010: start control
2.011: state control
2.012: invert control
3.xxx: 3-bit controlled
3.007: dimming control
3.008: blind control
4.xxx: character
4.001: character (ASCII)
4.002: character (ISO 8859-1)
5.xxx: 8-bit unsigned value
5.001: percentage (0..100%)
5.003: angle (degrees)
5.004: percentage (0..255%)
5.005: ratio (0..255)
5.006: tariff (0..255)
5.010: counter pulses (0..255)
5.100: fan stage (0..255)
6.xxx: 8-bit signed value
6.001: percentage (-128..127%)
6.010: counter pulses (-128..127)
6.020: status with mode
7.xxx: 2-byte unsigned value
7.001: pulses
7.002: time (ms)
7.003: time (10 ms)
7.004: time (100 ms)
7.005: time (s)
7.006: time (min)
7.007: time (h)
7.010: property data type
7.011: length (mm)
7.012: current (mA)
7.013: brightness (lux)
7.600: absolute colour temperature (K)
8.xxx: 2-byte signed value
8.001: pulses difference
8.002: time lag (ms)
8.003: time lag(10 ms)
8.004: time lag (100 ms)
8.005: time lag (s)
8.006: time lag (min)
8.007: time lag (h)
8.010: percentage difference (%)
8.011: rotation angle (°)
8.012: length (m)
9.xxx: 2-byte float value
9.001: temperature (°C)
9.002: temperature difference (K)
9.003: kelvin/hour (K/h)
9.004: lux (Lux)
9.005: speed (m/s)
9.006: pressure (Pa)
9.007: humidity (%)
9.008: parts/million (ppm)
9.009: air flow (m³/h)
9.010: time (s)
9.011: time (ms)
9.020: voltage (mV)
9.021: current (mA)
9.022: power density (W/m²)
9.023: kelvin/percent (K/%)
9.024: power (kW)
9.025: volume flow (l/h)
9.026: rain amount (l/m²)
9.027: temperature (°F)
9.028: wind speed (km/h)
9.029: absolute humidity (g/m³)
9.030: concentration (µg/m³)
9.031: coefficient
10.xxx: time
10.001: time of day
11.xxx: date
11.001: date
12.xxx: 4-byte unsigned value
12.001: counter pulses (unsigned)
12.100: counter timesec (s)
12.101: counter timemin (min)
12.102: counter timehrs (h)
12.1200: volume liquid (l)
12.1201: volume (m³)
13.xxx: 4-byte signed value
13.001: counter pulses (signed)
13.002: flow rate (m³/h)
13.010: active energy (Wh)
13.011: apparant energy (VAh)
13.012: reactive energy (VARh)
13.013: active energy (kWh)
13.014: apparant energy (kVAh)
13.015: reactive energy (kVARh)
13.016: active energy (MWh)
13.100: time lag (s)
13.1200: delta volume liquid (l)
13.1201: delta volume (m³)
14.xxx: 4-byte float value
14.000: acceleration (m/s²)
14.001: angular acceleration (rad/s²)
14.002: activation energy (J/mol)
14.003: radioactive activity (1/s)
14.004: amount of substance (mol)
14.005: amplitude
14.006: angle (radiant)
14.007: angle (degree)
14.008: angular momentum (Js)
14.009: angular velocity (rad/s)
14.010: area (m*m)
14.011: capacitance (F)
14.012: flux density (C/m²)
14.013: charge density (C/m³)
14.014: compressibility (m²/N)
14.015: conductance (S)
14.016: conductivity (S/m)
14.017: density (kg/m³)
14.018: electric charge (C)
14.019: electric current (A)
14.020: electric current density (A/m²)
14.021: electric dipole moment (Cm)
14.022: electric displacement (C/m²)
14.023: electric field strength (V/m)
14.024: electric flux (C)
14.025: electric flux density (C/m²)
14.026: electric polarization (C/m²)
14.027: electric potential (V)
14.028: electric potential difference (V)
14.029: electromagnetic moment (Am²)
14.030: electromotive force (V)
14.031: energy (J)
14.032: force (N)
14.033: frequency (Hz)
14.034: angular frequency (rad/s)
14.035: heat capacity (J/K)
14.036: heat flow rate (W)
14.037: heat quantity
14.038: impedance (Ω)
14.039: length (m)
14.040: light quantity (J)
14.041: luminance (cd/m²)
14.042: luminous flux (lm)
14.043: luminous intensity (cd)
14.044: magnetic field strength (A/m)
14.045: magnetic flux (Wb)
14.046: magnetic flux density (T)
14.047: magnetic moment (Am²)
14.048: magnetic polarization (T)
14.049: magnetization (A/m)
14.050: magnetomotive force (A)
14.051: mass (kg)
14.052: mass flux (kg/s)
14.053: momentum (N/s)
14.054: phase angle (rad)
14.055: phase angle (°)
14.056: power (W)
14.057: power factor (cos Φ)
14.058: pressure (Pa)
14.059: reactance (Ω)
14.060: resistance (Ω)
14.061: resistivity (Ωm)
14.062: self inductance (H)
14.063: solid angle (sr)
14.064: sound intensity (W/m²)
14.065: speed (m/s)
14.066: stress (Pa)
14.067: surface tension (N/m)
14.068: temperature (°C)
14.069: temperature absolute (K)
14.070: temperature difference (K)
14.071: thermal capacity (J/K)
14.072: thermal conductivity (W/mK)
14.073: thermoelectric power (V/K)
14.074: time (s)
14.075: torque (Nm)
14.076: volume (m³)
14.077: volume flux (m³/s)
14.078: weight (N)
14.079: work (J)
14.1200: volume flux for meters (m³/h)
14.1201: volume flux for meters (1/ls)
15.xxx: entrance access
15.000: entrance access
16.xxx: character string
16.000: Character String (ASCII)
16.001: Character String (ISO 8859-1)
17.xxx: scene number
17.001: scene number
18.xxx: scene control
18.001: scene control
19.xxx: Date Time
19.001: date time
20.xxx: 1-byte
20.001: SCLO mode
20.002: building mode
20.003: occupied
20.004: priority
20.005: light application mode
20.006: light application area
20.007: alarm class
20.008: PSU mode
20.011: system error class
20.012: HVAC error class
20.013: time delay
20.014: wind force scale (0..12)
20.017: sensor mode
20.020: actuator connect type
20.021: cloud cover
20.022: power return mode
20.100: fuel type
20.101: burner type
20.102: HVAC mode
20.103: DHW mode
20.104: load priority
20.105: HVAC control mode
20.106: HVAC emergency mode
20.107: changeover mode
20.108: valve mode
20.109: damper mode
20.110: heater mode
20.111: fan mode
20.112: master/slave mode
20.113: status room setpoint
20.114: metering device type
20.115: hum dehum mode
20.116: enable H/C stage
20.120: ADA type
20.121: backup mode
20.122: start syncronization type
20.600: behavior lock/unlock
20.601: behavior bus power up/down
20.602: dali fade time
20.603: blink mode
20.604: light control mode
20.605: PB switch mode
20.606: PB action mode
20.607: PB dimm mode
20.608: switch on mode
20.609: load type
20.610: load type detection
20.611: converter test control
20.801: SAB except behavior
20.802: SAB behavior on lock/unlock
20.803: SSSB mode
20.804: blinds control mode
20.1000: communication mode
20.1001: additional information type
20.1002: RF mode selection
20.1003: RF filter mode selection
21.xxx: 8-bit set
21.001: general status
21.002: device control
21.100: forcing signal
21.101: forcing signal cool
21.102: room heating controller status
21.103: solar DHW controller status
21.104: fuel type set
21.105: room cooling controller status
21.106: ventilation controller status
21.107: combined status RTSM
21.601: lighting actuator error information
21.1000: RF communication mode info
21.1001: cEMI server supported RF filtering modes
21.1010: channel activation for 8 channels
22.xxx: 16-bit set
22.100: DHW controller status
22.101: RHCC status
22.102: combined status HVA
22.103: combined status RTC
22.1000: media
22.1010: channel activation for 16 channels
23.xxx: 2-bit set
23.001: on/off action
23.002: alarm reaction
23.003: up/down action
23.102: HVAC push button action
24.xxx:
24.001: Variable-Length ISO-8859-1 String
25.xxx: 2-nibble set
25.1000: busy/nak repetitions
26.xxx: 8-bit set
26.001: scene information
27.xxx: 32-bit set
27.001: bit-combined info on/off
28.xxx:
28.001: Unicode UTF-8 String
29.xxx: electrical energy
29.010: active energy (Wh)
29.011: apparant energy (VAh)
29.012: reactive energy (VARh)
30.xxx: 24 times channel activation
30.1010: activation state 0..23
206.xxx: 16-bit unsigned value & 8-bit enum
206.100: time delay & HVAC mode
206.102: time delay & DHW mode
206.104: time delay & occupancy mode
206.105: time delay & building mode
207.xxx: 8-bit unsigned value & 8-bit enum
207.600: Status Lighting Actuator
217.xxx: datapoint type version
217.001: DPT version
219.xxx: alarm info
219.001: alarm info
222.xxx: 3x 2-byte float value
222.100: room temperature setpoint
222.101: room temperature setpoint shift
225.xxx: scaling speed
225.001: scaling speed
225.002: scaling step time
229.xxx: 4-1-1 byte combined information
229.001: metering value (value,encoding,cmd)
230.xxx: MBus address
230.1000: MBus address
232.xxx: 3-byte colour RGB
232.600: RGB value 3x(0..255)
234.xxx: language code ISO 639-1
234.001: language code (ASCII)
235.xxx: Signed value with classification and validity
235.001: electrical energy with tariff
236.xxx: Prioritised Mode Control
236.001: priority control
237.xxx: configuration/ diagnostics
237.600: diagnostic value
238.xxx: configuration/ diagnostics
238.600: diagnostic value
240.xxx: positions
240.800: combined position
241.xxx: status
241.800: status sunblind & shutter actuator
242.xxx: status
242.600: colour xyY
244.xxx: Converter Status
244.600: DALI converter status
245.xxx: Converter test result
245.600: DALI converter test result
246.xxx: Battery Information
246.600: Battery Information
249.xxx: brightness colour temperature transition
249.600: brightness colour temperature transition
250.xxx: status
250.600: brightness colour temperature control
251.xxx: Colour RGBW
251.600: RGBW value 4x(0..100%)
252.xxx: Relative Control RGBW
252.600: RGBW relative control
254.xxx: Relative Control RGB
254.600: RGB relative control
255.xxx: F32F32
255.001: geographical location (longitude and latitude) expressed in degrees
275.xxx: F16F16F16F16
275.100: Temperature setpoint setting for 4 HVAC Modes
275.101: Temperature setpoint shift setting for 4 HVAC Modes

## Index_IfType (hidden)
Usb
IpTunneling
IpRouting

## Index_ObjType (hidden)
Switch
Dimming
Curtain
Value
EnableCtl

## Index_TgtType (hidden)
Switch
Dimming
Value
Scene