## Interfaces
InterfaceCode | InterfaceName | InterfaceType | InterfaceAddress | Port
接口编号 | 接口名称 | 接口类型 | 接口地址 | 端口
If_ZYnk | 内科住院楼 | IpTunnel | 172.20.200.249 | 3671
If_ZYwk | 外科住院楼 | IpTunnel | 172.20.160.249 | 3671
If_ZYzh | 综合住院楼 | IpTunnel | 172.20.120.249 | 3671
If_MZ | 门诊医技楼 | IpTunnel | 172.20.3.249 | 3671
If_JZ | 急诊楼 | IpTunnel | 172.20.87.249 | 3671
If_GR | 感染楼 | IpTunnel | 172.20.94.249 | 3671
If_JK | 健康管理中心 | IpTunnel | 172.20.65.249 | 3671
Note on D1: 默认广播IP：224.0.23.12

## Areas
MainCode | MainArea | MiddleCode | MiddleArea | SubCode | SubArea | AreaCode
主区域编号 | 主区域名称 | 中区域编号 | 中区域名称 | 子区域编号 | 子区域名称 | 区域编号
JG | 室外景观 |  |  |  |  | JG
ZYnk | 内科住院楼 |  |  |  |  | ZYnk
ZYnk | 内科住院楼 | LH | 亮化 |  |  | ZYnk.LH
ZYwk | 外科住院楼 |  |  |  |  | ZYwk
ZYwk | 外科住院楼 | LH | 亮化 |  |  | ZYwk.LH
ZYzh | 综合住院楼 |  |  |  |  | ZYzh
ZYzh | 综合住院楼 | LH | 亮化 |  |  | ZYzh.LH
ZYzh | 综合住院楼 | KYDT | 康养大厅 |  |  | ZYzh.KYDT
MZ | 门诊医技楼 |  |  |  |  | MZ
MZ | 门诊医技楼 | LH | 亮化 |  |  | MZ.LH
MZ | 门诊医技楼 | GG | 公共照明 |  |  | MZ.GG
MZ | 门诊医技楼 | GG | 公共照明 | F01 | F01 | MZ.GG.F01
MZ | 门诊医技楼 | GG | 公共照明 | F02 | F02 | MZ.GG.F02
MZ | 门诊医技楼 | GG | 公共照明 | F03 | F03 | MZ.GG.F03
MZ | 门诊医技楼 | GG | 公共照明 | F04 | F04 | MZ.GG.F04
JZ | 急诊楼 |  |  |  |  | JZ
JZ | 急诊楼 | LH | 亮化 |  |  | JZ.LH
GR | 感染楼 |  |  |  |  | GR
GR | 感染楼 | LH | 亮化 |  |  | GR.LH
JK | 健康管理中心 |  |  |  |  | JK
JK | 健康管理中心 | LH | 亮化 |  |  | JK.LH
FR | 发热门诊 |  |  |  |  | FR
FR | 发热门诊 | LH | 亮化 |  |  | FR.LH

## Objects
AreaCode | InterfaceCode | ObjectCode | ObjectType | ObjectName | GrpDpt-Sw | GrpAddr-Sw_Ctl | GrpAddr-Sw_Fdb | GrpDpt-Val | GrpAddr-Val_Ctl | GrpAddr-Val_Fdb
区域编号 | 接口编号 | 对象编号 | 对象类型 | 对象名称 | 开关-地址类型 | 开关-控制地址 | 开关-反馈地址 | 数值-地址类型 | 数值-控制地址 | 数值-反馈地址
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_101 | Switch | F03亮化灯 | 1.001: switch | 1/7/1 | 1/7/101
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_102 | Switch | 楼顶亮化灯 | 1.001: switch | 1/7/2 | 1/7/102
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_103 | Switch | 亮化分控 | 1.001: switch | 1/7/3 | 1/7/103
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_104 | Switch | F04亮化灯 | 1.001: switch | 1/7/4 | 1/7/104
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_105 | Switch | F05亮化灯 | 1.001: switch | 1/7/5 | 1/7/105
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_106 | Switch | F06亮化灯 | 1.001: switch | 1/7/6 | 1/7/106
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_107 | Switch | F07亮化灯 | 1.001: switch | 1/7/7 | 1/7/107
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_108 | Switch | F08亮化灯 | 1.001: switch | 1/7/8 | 1/7/108
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_109 | Switch | F09亮化灯 | 1.001: switch | 1/7/9 | 1/7/109
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_110 | Switch | F10亮化灯 | 1.001: switch | 1/7/10 | 1/7/110
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_111 | Switch | 楼号数字8 | 1.001: switch | 1/7/11 | 1/7/111
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_112 | Switch |  | 1.001: switch | 1/7/12 | 1/7/112
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_201 | Switch |  | 1.001: switch | 1/7/13 | 1/7/113
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_202 | Switch |  | 1.001: switch | 1/7/14 | 1/7/114
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_203 | Switch |  | 1.001: switch | 1/7/15 | 1/7/115
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_204 | Switch |  | 1.001: switch | 1/7/16 | 1/7/116
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_205 | Switch |  | 1.001: switch | 1/7/17 | 1/7/117
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_206 | Switch |  | 1.001: switch | 1/7/18 | 1/7/118
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_207 | Switch | 门厅字 | 1.001: switch | 1/7/19 | 1/7/119
ZYnk.LH | If_ZYnk | ZYnk_WDALJG1_208 | Switch |  | 1.001: switch | 1/7/20 | 1/7/120
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_101 | Switch | 楼顶亮化灯 | 1.001: switch | 1/7/21 | 1/7/121
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_102 | Switch | 楼名大字 | 1.001: switch | 1/7/22 | 1/7/122
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_103 | Switch | 楼号数字8 | 1.001: switch | 1/7/23 | 1/7/123
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_104 | Switch |  | 1.001: switch | 1/7/24 | 1/7/124
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_105 | Switch |  | 1.001: switch | 1/7/25 | 1/7/125
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_106 | Switch |  | 1.001: switch | 1/7/26 | 1/7/126
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_107 | Switch |  | 1.001: switch | 1/7/27 | 1/7/127
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_108 | Switch |  | 1.001: switch | 1/7/28 | 1/7/128
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_109 | Switch |  | 1.001: switch | 1/7/29 | 1/7/129
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_110 | Switch |  | 1.001: switch | 1/7/30 | 1/7/130
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_111 | Switch |  | 1.001: switch | 1/7/31 | 1/7/131
ZYnk.LH | If_ZYnk | ZYnk_WDALJG2_112 | Switch |  | 1.001: switch | 1/7/32 | 1/7/132
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_101 | Switch | F05亮化灯 | 1.001: switch | 2/7/1 | 2/7/101
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_102 | Switch | 楼号数字7 | 1.001: switch | 2/7/2 | 2/7/102
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_103 | Switch | F03亮化灯 | 1.001: switch | 2/7/3 | 2/7/103
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_104 | Switch | F04亮化灯 | 1.001: switch | 2/7/4 | 2/7/104
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_105 | Switch | 亮化分控 | 1.001: switch | 2/7/5 | 2/7/105
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_106 | Switch | F06亮化灯 | 1.001: switch | 2/7/6 | 2/7/106
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_107 | Switch | F07亮化灯 | 1.001: switch | 2/7/7 | 2/7/107
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_108 | Switch | F08亮化灯 | 1.001: switch | 2/7/8 | 2/7/108
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_109 | Switch | F09亮化灯 | 1.001: switch | 2/7/9 | 2/7/109
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_110 | Switch | F10亮化灯 | 1.001: switch | 2/7/10 | 2/7/110
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_111 | Switch |  | 1.001: switch | 2/7/11 | 2/7/111
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_112 | Switch |  | 1.001: switch | 2/7/12 | 2/7/112
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_201 | Switch |  | 1.001: switch | 2/7/13 | 2/7/113
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_202 | Switch |  | 1.001: switch | 2/7/14 | 2/7/114
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_203 | Switch |  | 1.001: switch | 2/7/15 | 2/7/115
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_204 | Switch |  | 1.001: switch | 2/7/16 | 2/7/116
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_205 | Switch |  | 1.001: switch | 2/7/17 | 2/7/117
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_206 | Switch |  | 1.001: switch | 2/7/18 | 2/7/118
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_207 | Switch | 门厅字 | 1.001: switch | 2/7/19 | 2/7/119
ZYwk.LH | If_ZYwk | ZYwk_WDALJG3_208 | Switch |  | 1.001: switch | 2/7/20 | 2/7/120
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_101 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/21 | 2/7/121
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_102 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/22 | 2/7/122
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_103 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/23 | 2/7/123
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_104 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/24 | 2/7/124
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_105 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/25 | 2/7/125
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_106 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/26 | 2/7/126
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_107 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/27 | 2/7/127
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_108 | Switch | 楼顶亮化灯 | 1.001: switch | 2/7/28 | 2/7/128
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_109 | Switch | 楼号数字7 | 1.001: switch | 2/7/29 | 2/7/129
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_110 | Switch |  | 1.001: switch | 2/7/30 | 2/7/130
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_111 | Switch |  | 1.001: switch | 2/7/31 | 2/7/131
ZYwk.LH | If_ZYwk | ZYwk_WDALJG4_112 | Switch |  | 1.001: switch | 2/7/32 | 2/7/132
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_101 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/1 | 3/7/101
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_102 | Switch |  | 1.001: switch | 3/7/2 | 3/7/102
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_103 | Switch |  | 1.001: switch | 3/7/3 | 3/7/103
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_104 | Switch | F04亮化灯 | 1.001: switch | 3/7/4 | 3/7/104
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_105 | Switch |  | 1.001: switch | 3/7/5 | 3/7/105
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_106 | Switch | F06亮化灯 | 1.001: switch | 3/7/6 | 3/7/106
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_107 | Switch |  | 1.001: switch | 3/7/7 | 3/7/107
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_108 | Switch | F08亮化灯 | 1.001: switch | 3/7/8 | 3/7/108
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_109 | Switch | F09亮化灯 | 1.001: switch | 3/7/9 | 3/7/109
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_110 | Switch | F10亮化灯 | 1.001: switch | 3/7/10 | 3/7/110
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_111 | Switch | F05亮化灯 | 1.001: switch | 3/7/11 | 3/7/111
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_112 | Switch |  | 1.001: switch | 3/7/12 | 3/7/112
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_201 | Switch | F07亮化灯 | 1.001: switch | 3/7/13 | 3/7/113
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_202 | Switch | 亮化分控 | 1.001: switch | 3/7/14 | 3/7/114
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_203 | Switch | F03亮化灯 | 1.001: switch | 3/7/15 | 3/7/115
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_204 | Switch | 楼号数字6 | 1.001: switch | 3/7/16 | 3/7/116
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_205 | Switch |  | 1.001: switch | 3/7/17 | 3/7/117
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_206 | Switch | 门厅字 | 1.001: switch | 3/7/18 | 3/7/118
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_207 | Switch |  | 1.001: switch | 3/7/19 | 3/7/119
ZYzh.LH | If_ZYzh | ZYzh_WDALJG5_208 | Switch |  | 1.001: switch | 3/7/20 | 3/7/120
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_101 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/21 | 3/7/121
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_102 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/22 | 3/7/122
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_103 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/23 | 3/7/123
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_104 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/24 | 3/7/124
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_105 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/25 | 3/7/125
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_106 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/26 | 3/7/126
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_107 | Switch | 楼顶亮化灯 | 1.001: switch | 3/7/27 | 3/7/127
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_108 | Switch | 楼顶大字 | 1.001: switch | 3/7/28 | 3/7/128
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_109 | Switch | 楼顶大字 | 1.001: switch | 3/7/29 | 3/7/129
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_110 | Switch | 楼顶大字 | 1.001: switch | 3/7/30 | 3/7/130
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_111 | Switch | 楼号数字6 | 1.001: switch | 3/7/31 | 3/7/131
ZYzh.LH | If_ZYzh | ZYzh_WDALJG6_112 | Switch |  | 1.001: switch | 3/7/32 | 3/7/132
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_101 | Switch |  | 1.001: switch | 3/1/1 | 3/1/101
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_102 | Switch |  | 1.001: switch | 3/1/2 | 3/1/102
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_103 | Switch |  | 1.001: switch | 3/1/3 | 3/1/103
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_104 | Switch |  | 1.001: switch | 3/1/4 | 3/1/104
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_105 | Switch |  | 1.001: switch | 3/1/5 | 3/1/105
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_106 | Switch |  | 1.001: switch | 3/1/6 | 3/1/106
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_107 | Switch |  | 1.001: switch | 3/1/7 | 3/1/107
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_108 | Switch |  | 1.001: switch | 3/1/8 | 3/1/108
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_109 | Switch |  | 1.001: switch | 3/1/9 | 3/1/109
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_110 | Switch |  | 1.001: switch | 3/1/10 | 3/1/110
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_111 | Switch |  | 1.001: switch | 3/1/11 | 3/1/111
ZYzh.KYDT | If_ZYzh | ZYzh_KYDT_112 | Switch |  | 1.001: switch | 3/1/12 | 3/1/112
MZ.LH | If_MZ | MZ_5WDMALJG1_101 | Switch | 抱柱灯西3 | 1.001: switch | 4/7/1 | 4/7/101
MZ.LH | If_MZ | MZ_5WDMALJG1_102 | Switch | 抱柱灯西4 | 1.001: switch | 4/7/2 | 4/7/102
MZ.LH | If_MZ | MZ_5WDMALJG1_103 | Switch | 抱柱灯东4 | 1.001: switch | 4/7/3 | 4/7/103
MZ.LH | If_MZ | MZ_5WDMALJG1_104 | Switch | 抱柱灯东4 | 1.001: switch | 4/7/4 | 4/7/104
MZ.LH | If_MZ | MZ_5WDMALJG1_105 | Switch | 楼顶线条灯 | 1.001: switch | 4/7/5 | 4/7/105
MZ.LH | If_MZ | MZ_5WDMALJG1_106 | Switch | 楼顶线条灯 | 1.001: switch | 4/7/6 | 4/7/106
MZ.LH | If_MZ | MZ_5WDMALJG1_107 | Switch | 楼顶线条灯 | 1.001: switch | 4/7/7 | 4/7/107
MZ.LH | If_MZ | MZ_5WDMALJG1_108 | Switch | 一楼抱柱灯 | 1.001: switch | 4/7/8 | 4/7/108
MZ.LH | If_MZ | MZ_5WDMALJG1_109 | Switch |  | 1.001: switch | 4/7/9 | 4/7/109
MZ.LH | If_MZ | MZ_5WDMALJG1_110 | Switch |  | 1.001: switch | 4/7/10 | 4/7/110
MZ.LH | If_MZ | MZ_5WDMALJG1_111 | Switch |  | 1.001: switch | 4/7/11 | 4/7/111
MZ.LH | If_MZ | MZ_5WDMALJG1_112 | Switch |  | 1.001: switch | 4/7/12 | 4/7/112
MZ.LH | If_MZ | MZ_5WDMALJG1_201 | Switch | 楼号数字1 | 1.001: switch | 4/7/13 | 4/7/113
MZ.LH | If_MZ | MZ_5WDMALJG1_202 | Switch |  | 1.001: switch | 4/7/14 | 4/7/114
MZ.LH | If_MZ | MZ_5WDMALJG1_203 | Switch |  | 1.001: switch | 4/7/15 | 4/7/115
MZ.LH | If_MZ | MZ_5WDMALJG1_204 | Switch |  | 1.001: switch | 4/7/16 | 4/7/116
MZ.LH | If_MZ | MZ_5WDMALJG6_101 | Switch | 儿科大字 | 1.001: switch | 4/7/17 | 4/7/117
MZ.LH | If_MZ | MZ_5WDMALJG6_102 | Switch | 抱柱灯 | 1.001: switch | 4/7/18 | 4/7/118
MZ.LH | If_MZ | MZ_5WDMALJG6_103 | Switch | 楼号数字1 | 1.001: switch | 4/7/19 | 4/7/119
MZ.LH | If_MZ | MZ_5WDMALJG6_104 | Switch | 云纹东上 | 1.001: switch | 4/7/20 | 4/7/120
MZ.LH | If_MZ | MZ_5WDMALJG6_105 | Switch | 云纹西下 | 1.001: switch | 4/7/21 | 4/7/121
MZ.LH | If_MZ | MZ_5WDMALJG6_106 | Switch | 云纹东下 | 1.001: switch | 4/7/22 | 4/7/122
MZ.LH | If_MZ | MZ_5WDMALJG6_107 | Switch | 云纹西下 | 1.001: switch | 4/7/23 | 4/7/123
MZ.LH | If_MZ | MZ_5WDMALJG6_108 | Switch | 分控 | 1.001: switch | 4/7/24 | 4/7/124
MZ.LH | If_MZ | MZ_5WDMALJG6_109 | Switch | 门诊大字 | 1.001: switch | 4/7/25 | 4/7/125
MZ.LH | If_MZ | MZ_5WDMALJG6_110 | Switch | 抱柱灯 | 1.001: switch | 4/7/26 | 4/7/126
MZ.LH | If_MZ | MZ_5WDMALJG6_111 | Switch |  | 1.001: switch | 4/7/27 | 4/7/127
MZ.LH | If_MZ | MZ_5WDMALJG6_112 | Switch |  | 1.001: switch | 4/7/28 | 4/7/128
MZ.LH | If_MZ | MZ_5WDMALJG6_201 | Switch | 楼顶大字 | 1.001: switch | 4/7/29 | 4/7/129
MZ.LH | If_MZ | MZ_5WDMALJG6_202 | Switch |  | 1.001: switch | 4/7/30 | 4/7/130
MZ.LH | If_MZ | MZ_5WDMALJG6_203 | Switch |  | 1.001: switch | 4/7/31 | 4/7/131
MZ.LH | If_MZ | MZ_5WDMALJG6_204 | Switch |  | 1.001: switch | 4/7/32 | 4/7/132
JZ.LH | If_JZ | JZ_WDZALJG1_101 | Switch | 行政大字 | 1.001: switch | 5/7/1 | 5/7/101
JZ.LH | If_JZ | JZ_WDZALJG1_102 | Switch | F02亮化灯 | 1.001: switch | 5/7/2 | 5/7/102
JZ.LH | If_JZ | JZ_WDZALJG1_103 | Switch | 分控 | 1.001: switch | 5/7/3 | 5/7/103
JZ.LH | If_JZ | JZ_WDZALJG1_104 | Switch | 北转角灯 | 1.001: switch | 5/7/4 | 5/7/104
JZ.LH | If_JZ | JZ_WDZALJG1_105 | Switch | 急诊F02大字 | 1.001: switch | 5/7/5 | 5/7/105
JZ.LH | If_JZ | JZ_WDZALJG1_106 | Switch | 楼顶亮化灯 | 1.001: switch | 5/7/6 | 5/7/106
JZ.LH | If_JZ | JZ_WDZALJG1_107 | Switch | 楼顶亮化灯 | 1.001: switch | 5/7/7 | 5/7/107
JZ.LH | If_JZ | JZ_WDZALJG1_108 | Switch | 楼顶亮化灯 | 1.001: switch | 5/7/8 | 5/7/108
JZ.LH | If_JZ | JZ_WDZALJG1_109 | Switch | 楼号数字3 | 1.001: switch | 5/7/9 | 5/7/109
JZ.LH | If_JZ | JZ_WDZALJG1_110 | Switch |  | 1.001: switch | 5/7/10 | 5/7/110
JZ.LH | If_JZ | JZ_WDZALJG1_111 | Switch | 楼顶大字 | 1.001: switch | 5/7/11 | 5/7/111
JZ.LH | If_JZ | JZ_WDZALJG1_112 | Switch |  | 1.001: switch | 5/7/12 | 5/7/112
JZ.LH | If_JZ | JZ_4JZALJG2_101 | Switch | 东侧线条灯 | 1.001: switch | 5/7/13 | 5/7/113
JZ.LH | If_JZ | JZ_4JZALJG2_102 | Switch | 转角灯南侧 | 1.001: switch | 5/7/14 | 5/7/114
JZ.LH | If_JZ | JZ_4JZALJG2_103 | Switch | F02亮化灯 | 1.001: switch | 5/7/15 | 5/7/115
JZ.LH | If_JZ | JZ_4JZALJG2_104 | Switch | 西侧线条灯 | 1.001: switch | 5/7/16 | 5/7/116
JZ.LH | If_JZ | JZ_4JZALJG2_105 | Switch | 南侧线条灯 | 1.001: switch | 5/7/17 | 5/7/117
JZ.LH | If_JZ | JZ_4JZALJG2_106 | Switch | 分控 | 1.001: switch | 5/7/18 | 5/7/118
JZ.LH | If_JZ | JZ_4JZALJG2_107 | Switch |  | 1.001: switch | 5/7/19 | 5/7/119
JZ.LH | If_JZ | JZ_4JZALJG2_108 | Switch |  | 1.001: switch | 5/7/20 | 5/7/120
JZ.LH | If_JZ | JZ_4JZALJG2_109 | Switch |  | 1.001: switch | 5/7/21 | 5/7/121
JZ.LH | If_JZ | JZ_4JZALJG2_110 | Switch |  | 1.001: switch | 5/7/22 | 5/7/122
JZ.LH | If_JZ | JZ_4JZALJG2_111 | Switch | 楼顶大字 | 1.001: switch | 5/7/23 | 5/7/123
JZ.LH | If_JZ | JZ_4JZALJG2_112 | Switch |  | 1.001: switch | 5/7/24 | 5/7/124
GR.LH | If_GR | GR_WDGRALJG_101 | Switch | 楼顶亮化灯 | 1.001: switch | 6/7/1 | 6/7/101
GR.LH | If_GR | GR_WDGRALJG_102 | Switch | 楼顶亮化灯 | 1.001: switch | 6/7/2 | 6/7/102
GR.LH | If_GR | GR_WDGRALJG_103 | Switch | 楼顶亮化灯 | 1.001: switch | 6/7/3 | 6/7/103
GR.LH | If_GR | GR_WDGRALJG_104 | Switch | 楼顶亮化灯 | 1.001: switch | 6/7/4 | 6/7/104
GR.LH | If_GR | GR_WDGRALJG_105 | Switch | 北侧大字 | 1.001: switch | 6/7/5 | 6/7/105
GR.LH | If_GR | GR_WDGRALJG_106 | Switch | 东侧大字 | 1.001: switch | 6/7/6 | 6/7/106
GR.LH | If_GR | GR_WDGRALJG_107 | Switch | 门头字 | 1.001: switch | 6/7/7 | 6/7/107
GR.LH | If_GR | GR_WDGRALJG_108 | Switch | 门头字 | 1.001: switch | 6/7/8 | 6/7/108
GR.LH | If_GR | GR_WDGRALJG_109 | Switch | 门头字 | 1.001: switch | 6/7/9 | 6/7/109
GR.LH | If_GR | GR_WDGRALJG_110 | Switch |  | 1.001: switch | 6/7/10 | 6/7/110
GR.LH | If_GR | GR_WDGRALJG_111 | Switch |  | 1.001: switch | 6/7/11 | 6/7/111
GR.LH | If_GR | GR_WDGRALJG_112 | Switch |  | 1.001: switch | 6/7/12 | 6/7/112
JK.LH | If_JK | JK_WDJKALJG_101 | Switch | 分控 | 1.001: switch | 7/7/1 | 7/7/101
JK.LH | If_JK | JK_WDJKALJG_102 | Switch | 线条灯 | 1.001: switch | 7/7/2 | 7/7/102
JK.LH | If_JK | JK_WDJKALJG_103 | Switch | 线条灯 | 1.001: switch | 7/7/3 | 7/7/103
JK.LH | If_JK | JK_WDJKALJG_104 | Switch | F04~F05亮化灯 | 1.001: switch | 7/7/4 | 7/7/104
JK.LH | If_JK | JK_WDJKALJG_105 | Switch | F02~F03亮化灯 | 1.001: switch | 7/7/5 | 7/7/105
JK.LH | If_JK | JK_WDJKALJG_106 | Switch | 分控 | 1.001: switch | 7/7/6 | 7/7/106
JK.LH | If_JK | JK_WDJKALJG_107 | Switch | 南侧F01灯 | 1.001: switch | 7/7/7 | 7/7/107
JK.LH | If_JK | JK_WDJKALJG_108 | Switch | 楼号数字 | 1.001: switch | 7/7/8 | 7/7/108
JK.LH | If_JK | JK_WDJKALJG_109 | Switch | 西侧F01灯 | 1.001: switch | 7/7/9 | 7/7/109
JK.LH | If_JK | JK_WDJKALJG_110 | Switch |  | 1.001: switch | 7/7/10 | 7/7/110
JK.LH | If_JK | JK_WDJKALJG_111 | Switch | F02大字 | 1.001: switch | 7/7/11 | 7/7/111
JK.LH | If_JK | JK_WDJKALJG_112 | Switch |  | 1.001: switch | 7/7/12 | 7/7/112
JK.LH | If_JK | JK_WDJKALJG_201 | Switch |  | 1.001: switch | 7/7/13 | 7/7/113
JK.LH | If_JK | JK_WDJKALJG_202 | Switch | 楼顶大字-南 | 1.001: switch | 7/7/14 | 7/7/114
JK.LH | If_JK | JK_WDJKALJG_203 | Switch | 楼顶大字-东 | 1.001: switch | 7/7/15 | 7/7/115
JK.LH | If_JK | JK_WDJKALJG_204 | Switch |  | 1.001: switch | 7/7/16 | 7/7/116
FR.LH | If_GR | FR_WDALFRJG1_101 | Switch | F02大字 | 1.001: switch | 8/7/1 | 8/7/101
FR.LH | If_GR | FR_WDALFRJG1_102 | Switch | 楼顶大字 | 1.001: switch | 8/7/2 | 8/7/102
FR.LH | If_GR | FR_WDALFRJG1_103 | Switch | 楼顶大字 | 1.001: switch | 8/7/3 | 8/7/103
FR.LH | If_GR | FR_WDALFRJG1_104 | Switch |  | 1.001: switch | 8/7/4 | 8/7/104
FR.LH | If_GR | FR_WDALFRJG1_105 | Switch |  | 1.001: switch | 8/7/5 | 8/7/105
FR.LH | If_GR | FR_WDALFRJG1_106 | Switch |  | 1.001: switch | 8/7/6 | 8/7/106
FR.LH | If_GR | FR_WDALFRJG1_107 | Switch |  | 1.001: switch | 8/7/7 | 8/7/107
FR.LH | If_GR | FR_WDALFRJG1_108 | Switch |  | 1.001: switch | 8/7/8 | 8/7/108
JG | If_ZYwk | JG_1_101 | Switch | 射灯01 | 1.001: switch | 0/1/1 | 0/1/101
JG | If_ZYwk | JG_1_102 | Switch | 射灯02 | 1.001: switch | 0/1/2 | 0/1/102
JG | If_ZYwk | JG_1_103 | Switch | 射灯03 | 1.001: switch | 0/1/3 | 0/1/103
JG | If_ZYwk | JG_1_104 | Switch | 射灯04 | 1.001: switch | 0/1/4 | 0/1/104
JG | If_ZYwk | JG_1_105 | Switch | 射灯05 | 1.001: switch | 0/1/5 | 0/1/105
JG | If_ZYwk | JG_1_106 | Switch | 射灯06 | 1.001: switch | 0/1/6 | 0/1/106
JG | If_ZYwk | JG_1_107 | Switch | 射灯07 | 1.001: switch | 0/1/7 | 0/1/107
JG | If_ZYwk | JG_1_108 | Switch | 庭院灯01 | 1.001: switch | 0/1/8 | 0/1/108
JG | If_ZYwk | JG_1_201 | Switch | 庭院灯02 | 1.001: switch | 0/1/9 | 0/1/109
JG | If_ZYwk | JG_1_202 | Switch | 庭院灯03 | 1.001: switch | 0/1/10 | 0/1/110
JG | If_ZYwk | JG_1_203 | Switch | 庭院灯04 | 1.001: switch | 0/1/11 | 0/1/111
JG | If_ZYwk | JG_1_204 | Switch | 庭院灯05 | 1.001: switch | 0/1/12 | 0/1/112
JG | If_ZYwk | JG_1_205 | Switch | 庭院灯06 | 1.001: switch | 0/1/13 | 0/1/113
JG | If_ZYwk | JG_1_206 | Switch | 高杆灯01 | 1.001: switch | 0/1/14 | 0/1/114
JG | If_ZYwk | JG_1_207 | Switch | 高杆灯02 | 1.001: switch | 0/1/15 | 0/1/115
JG | If_ZYwk | JG_1_208 | Switch | 高杆灯03 | 1.001: switch | 0/1/16 | 0/1/116
JG | If_ZYwk | JG_1_301 | Switch | 高杆灯04 | 1.001: switch | 0/1/17 | 0/1/117
JG | If_ZYwk | JG_1_302 | Switch | 筒灯01 | 1.001: switch | 0/1/18 | 0/1/118
JG | If_ZYwk | JG_1_303 | Switch | 筒灯02 | 1.001: switch | 0/1/19 | 0/1/119
JG | If_ZYwk | JG_1_304 | Switch | 花架灯 | 1.001: switch | 0/1/20 | 0/1/120
JG | If_ZYwk | JG_1_305 | Switch | 高杆灯05 | 1.001: switch | 0/1/21 | 0/1/121
JG | If_ZYwk | JG_1_306 | Switch | 备用01 | 1.001: switch | 0/1/22 | 0/1/122
JG | If_ZYwk | JG_1_307 | Switch | 备用02 | 1.001: switch | 0/1/23 | 0/1/123
JG | If_ZYwk | JG_1_308 | Switch |  | 1.001: switch | 0/1/24 | 0/1/124
JG | If_MZ | JG_2_101 | Switch | 射灯01 | 1.001: switch | 0/1/25 | 0/1/101
JG | If_MZ | JG_2_102 | Switch | 射灯02 | 1.001: switch | 0/1/26 | 0/1/102
JG | If_MZ | JG_2_103 | Switch | 庭院灯01 | 1.001: switch | 0/1/27 | 0/1/103
JG | If_MZ | JG_2_104 | Switch | 庭院灯02 | 1.001: switch | 0/1/28 | 0/1/104
JG | If_MZ | JG_2_105 | Switch | 庭院灯03 | 1.001: switch | 0/1/29 | 0/1/105
JG | If_MZ | JG_2_106 | Switch | 高杆灯01 | 1.001: switch | 0/1/30 | 0/1/106
JG | If_MZ | JG_2_107 | Switch | 高杆灯02 | 1.001: switch | 0/1/31 | 0/1/107
JG | If_MZ | JG_2_108 | Switch | 高杆灯03 | 1.001: switch | 0/1/32 | 0/1/108
JG | If_MZ | JG_2_201 | Switch | 高杆灯04 | 1.001: switch | 0/1/33 | 0/1/109
JG | If_MZ | JG_2_202 | Switch | 灯带 | 1.001: switch | 0/1/34 | 0/1/110
JG | If_MZ | JG_2_203 | Switch | 灯箱 | 1.001: switch | 0/1/35 | 0/1/111
JG | If_MZ | JG_2_204 | Switch | 识别字 | 1.001: switch | 0/1/36 | 0/1/112
JG | If_MZ | JG_2_205 | Switch | 备用 | 1.001: switch | 0/1/37 | 0/1/113
JG | If_MZ | JG_2_206 | Switch | 备用 | 1.001: switch | 0/1/38 | 0/1/114
JG | If_MZ | JG_2_207 | Switch |  | 1.001: switch | 0/1/39 | 0/1/115
JG | If_MZ | JG_2_208 | Switch |  | 1.001: switch | 0/1/40 | 0/1/116
Note on B2: 对象支持对应多个接口但是不推荐，多个接口之间用英文逗号分隔。
Note on C2: 对象编号不允许重复

## Scenes
AreaCode | InterfaceCode | SceneCode | SceneName | GroupAddress | SceneValues
区域编号 | 接口编号 | 场景编号 | 场景名称 | 组地址 | 场景值
ZYnk.LH | If_ZYnk | Scn_1 | 内科住院楼亮化 | 1/0/100 | 0=全关,1=全开
ZYwk.LH | If_ZYwk | Scn_2 | 外科住院楼亮化 | 2/0/100 | 0=全关,1=全开
ZYzh.LH | If_ZYzh | Scn_3 | 综合住院楼亮化 | 3/0/100 | 0=全关,1=全开
MZ.LH | If_MZ | Scn_4 | 门诊医技楼亮化 | 4/0/100 | 0=全关,1=全开
JZ.LH | If_JZ | Scn_5 | 急诊楼亮化 | 5/0/100 | 0=全关,1=全开
GR.LH | If_GR | Scn_6 | 感染楼亮化 | 6/0/100 | 0=全关,1=全开
JK.LH | If_JK | Scn_7 | 健康管理中心亮化 | 7/0/100 | 0=全关,1=全开
FR.LH | If_GR | Scn_8 | 发热门诊亮化 | 8/0/100 | 0=全关,1=全开
JG | If_ZYwk,If_MZ | Scn_9 | 室外景观 | 0/0/100 | 0=全关,1=全开
MZ.GG | If_MZ | Scn_10 | 门诊医技楼_公共照明 | 4/0/10 | 0=全关,1=全开
ZYzh.F01.KYDT | If_ZYzh | Scn_11 | 综合住院楼_康养大厅 | 3/0/11 | 0=全关,1=全开
Note on B2: 场景支持对应多个接口，多个接口之间用英文逗号分隔。
Note on C2: 场景编号不允许重复
Note on E2: 场景可以有多个组地址，组地址之间用逗号分隔
Note on F2: [场景地址]=[场景名称] 多个场景之间用英文逗号分隔。

## Devices
AreaCode | InterfaceCode | DeviceCode | DeviceName | DeviceModel | IndividualAddress
区域编号 | 接口编号 | 设备编号 | 设备名称 | 设备型号 | 设备地址
ZYnk.LH | If_ZYnk | WDALJG1 | KNX网关&逻辑控制器 | LSS100200 | 1.1.0
ZYnk.LH | If_ZYnk | WDALJG1 | 开关模块 | MTN648493 | 1.1.11
ZYnk.LH | If_ZYnk | WDALJG1 | 开关模块 | MTN647893 | 1.1.12
ZYnk.LH | If_ZYnk | WDALJG2 | 开关模块 | MTN648493 | 1.1.21
ZYwk.LH | If_ZYwk | WDALJG3 | KNX网关 | MTN6500-0103 | 1.2.0
ZYwk.LH | If_ZYwk | WDALJG3 | 开关模块 | MTN648493 | 1.2.11
ZYwk.LH | If_ZYwk | WDALJG3 | 开关模块 | MTN647893 | 1.2.12
ZYwk.LH | If_ZYwk | WDALJG4 | 开关模块 | MTN648493 | 1.2.21
JG | If_ZYwk | JG1 | 开关模块 | MTN6705-0008 | 1.2.31
ZYzh.LH | If_ZYzh | WDALJG5 | KNX网关 | MTN6500-0103 | 1.3.0
ZYzh.LH | If_ZYzh | WDALJG5 | 开关模块 | MTN648493 | 1.3.11
ZYzh.LH | If_ZYzh | WDALJG5 | 开关模块 | MTN647893 | 1.3.12
ZYzh.LH | If_ZYzh | WDALJG6 | 开关模块 | MTN648493 | 1.3.21
ZYzh.KYDT | If_ZYzh | KYDT | 开关模块 | MTN648493 | 1.3.101
MZ.LH | If_MZ | 5WDMALJG1 | KNX网关&逻辑控制器 | LSS100200 | 1.4.0
MZ.LH | If_MZ | 5WDMALJG1 | 开关模块 | MTN648493 | 1.4.11
MZ.LH | If_MZ | 5WDMALJG1 | 开关模块 | MTN647593 | 1.4.12
MZ.LH | If_MZ | 5WDMALJG6 | 开关模块 | MTN648493 | 1.4.21
MZ.LH | If_MZ | 5WDMALJG6 | 开关模块 | MTN647593 | 1.4.22
JG | If_MZ | JG2 | 开关模块 | MTN6705-0008 | 1.4.31
JZ.LH | If_JZ | WDZALJG1 | KNX网关 | MTN6500-0103 | 1.5.0
JZ.LH | If_JZ | WDZALJG1 | 开关模块 | MTN648493 | 1.5.11
JZ.LH | If_JZ | 4JZALJG2 | 开关模块 | MTN648493 | 1.5.21
FR.LH | If_JZ | WDALFRJG1 | 开关模块 | MTN647893 | 1.5.31
GR | If_GR | WDGRALJG | KNX网关 | MTN6500-0103 | 1.6.0
GR | If_GR | WDGRALJG | 开关模块 | MTN648493 | 1.6.11
JK | If_JK | WDJKALJG | KNX网关 | MTN6500-0103 | 1.7.0
JK | If_JK | WDJKALJG | 开关模块 | MTN648493 | 1.7.11
JK | If_JK | WDJKALJG | 开关模块 | MTN647593 | 1.7.12
Note on B2: 设备所在接口的编号。

## Schedules
ScheduleCode | ScheduleName | TargetType | TargetCode | ScheduleEvents | Enable
定时编号 | 定时名称 | 目标对象类型 | 目标对象编号 | 定时事件 | 启用
Scd_1 | 内科住院楼亮化定时 | Scene | Scn_1 | 18:00=1,6:00=0 | 1
Scd_2 | 外科住院楼亮化定时 | Scene | Scn_2 | 18:00=1,6:00=0 | 1
Scd_3 | 综合住院楼亮化定时 | Scene | Scn_3 | 18:00=1,6:00=0 | 1
Scd_4 | 门诊医技楼亮化定时 | Scene | Scn_4 | 18:00=1,6:00=0 | 1
Scd_5 | 急诊楼亮化定时 | Scene | Scn_5 | 18:00=1,6:00=0 | 1
Scd_6 | 感染楼亮化定时 | Scene | Scn_6 | 18:00=1,6:00=0 | 1
Scd_7 | 健康管理中心亮化定时 | Scene | Scn_7 | 18:00=1,6:00=0 | 1
Scd_8 | 发热门诊亮化定时 | Scene | Scn_8 | 18:00=1,6:00=0 | 1
Scd_9 | 室外景观 | Scene | Scn_9 | 19:00=1,22:00=0 | 1
Scd_10 | 门诊医技楼_公共照明 | Scene | Scn_10 | 19:00=1,22:00=0 | 1
Scd_11 | 综合住院楼_康养大厅 | Scene | Scn_11 | 19:00=1,22:00=0 | 0

## Links
LinkName | LinkUrl | Account | Password
链接名称 | 链接地址 | 账号名 | 密码

## Index_DPT (hidden)
DatapointType
数据点类型
1.xxx: 1-bit
1.001: switch
1.002: boolean
1.003: enable
1.004: ramp
1.005: alarm
1.006: binary value
1.007: step
1.008: up/down
1.009: open/close
1.010: start/stop
1.011: state
1.012: invert
1.013: dim send style
1.014: input source
1.015: reset
1.016: acknowledge
1.017: trigger
1.018: occupancy
1.019: window/door
1.021: logical function
1.022: scene
1.023: shutter/blinds mode
1.024: day/night
1.100: cooling/heating
2.xxx: 1-bit controlled
2.001: switch control
2.002: boolean control
2.003: enable control
2.004: ramp control
2.005: alarm control
2.006: binary value control
2.007: step control
2.008: direction control 1
2.009: direction control 2
2.010: start control
2.011: state control
2.012: invert control
3.xxx: 3-bit controlled
3.007: dimming control
3.008: blind control
4.xxx: character
4.001: character (ASCII)
4.002: character (ISO 8859-1)
5.xxx: 8-bit unsigned value
5.001: percentage (0..100%)
5.003: angle (degrees)
5.004: percentage (0..255%)
5.005: ratio (0..255)
5.006: tariff (0..255)
5.010: counter pulses (0..255)
5.100: fan stage (0..255)
6.xxx: 8-bit signed value
6.001: percentage (-128..127%)
6.010: counter pulses (-128..127)
6.020: status with mode
7.xxx: 2-byte unsigned value
7.001: pulses
7.002: time (ms)
7.003: time (10 ms)
7.004: time (100 ms)
7.005: time (s)
7.006: time (min)
7.007: time (h)
7.010: property data type
7.011: length (mm)
7.012: current (mA)
7.013: brightness (lux)
7.600: absolute colour temperature (K)
8.xxx: 2-byte signed value
8.001: pulses difference
8.002: time lag (ms)
8.003: time lag(10 ms)
8.004: time lag (100 ms)
8.005: time lag (s)
8.006: time lag (min)
8.007: time lag (h)
8.010: percentage difference (%)
8.011: rotation angle (°)
8.012: length (m)
9.xxx: 2-byte float value
9.001: temperature (°C)
9.002: temperature difference (K)
9.003: kelvin/hour (K/h)
9.004: lux (Lux)
9.005: speed (m/s)
9.006: pressure (Pa)
9.007: humidity (%)
9.008: parts/million (ppm)
9.009: air flow (m³/h)
9.010: time (s)
9.011: time (ms)
9.020: voltage (mV)
9.021: current (mA)
9.022: power density (W/m²)
9.023: kelvin/percent (K/%)
9.024: power (kW)
9.025: volume flow (l/h)
9.026: rain amount (l/m²)
9.027: temperature (°F)
9.028: wind speed (km/h)
9.029: absolute humidity (g/m³)
9.030: concentration (µg/m³)
9.031: coefficient
10.xxx: time
10.001: time of day
11.xxx: date
11.001: date
12.xxx: 4-byte unsigned value
12.001: counter pulses (unsigned)
12.100: counter timesec (s)
12.101: counter timemin (min)
12.102: counter timehrs (h)
12.1200: volume liquid (l)
12.1201: volume (m³)
13.xxx: 4-byte signed value
13.001: counter pulses (signed)
13.002: flow rate (m³/h)
13.010: active energy (Wh)
13.011: apparant energy (VAh)
13.012: reactive energy (VARh)
13.013: active energy (kWh)
13.014: apparant energy (kVAh)
13.015: reactive energy (kVARh)
13.016: active energy (MWh)
13.100: time lag (s)
13.1200: delta volume liquid (l)
13.1201: delta volume (m³)
14.xxx: 4-byte float value
14.000: acceleration (m/s²)
14.001: angular acceleration (rad/s²)
14.002: activation energy (J/mol)
14.003: radioactive activity (1/s)
14.004: amount of substance (mol)
14.005: amplitude
14.006: angle (radiant)
14.007: angle (degree)
14.008: angular momentum (Js)
14.009: angular velocity (rad/s)
14.010: area (m*m)
14.011: capacitance (F)
14.012: flux density (C/m²)
14.013: charge density (C/m³)
14.014: compressibility (m²/N)
14.015: conductance (S)
14.016: conductivity (S/m)
14.017: density (kg/m³)
14.018: electric charge (C)
14.019: electric current (A)
14.020: electric current density (A/m²)
14.021: electric dipole moment (Cm)
14.022: electric displacement (C/m²)
14.023: electric field strength (V/m)
14.024: electric flux (C)
14.025: electric flux density (C/m²)
14.026: electric polarization (C/m²)
14.027: electric potential (V)
14.028: electric potential difference (V)
14.029: electromagnetic moment (Am²)
14.030: electromotive force (V)
14.031: energy (J)
14.032: force (N)
14.033: frequency (Hz)
14.034: angular frequency (rad/s)
14.035: heat capacity (J/K)
14.036: heat flow rate (W)
14.037: heat quantity
14.038: impedance (Ω)
14.039: length (m)
14.040: light quantity (J)
14.041: luminance (cd/m²)
14.042: luminous flux (lm)
14.043: luminous intensity (cd)
14.044: magnetic field strength (A/m)
14.045: magnetic flux (Wb)
14.046: magnetic flux density (T)
14.047: magnetic moment (Am²)
14.048: magnetic polarization (T)
14.049: magnetization (A/m)
14.050: magnetomotive force (A)
14.051: mass (kg)
14.052: mass flux (kg/s)
14.053: momentum (N/s)
14.054: phase angle (rad)
14.055: phase angle (°)
14.056: power (W)
14.057: power factor (cos Φ)
14.058: pressure (Pa)
14.059: reactance (Ω)
14.060: resistance (Ω)
14.061: resistivity (Ωm)
14.062: self inductance (H)
14.063: solid angle (sr)
14.064: sound intensity (W/m²)
14.065: speed (m/s)
14.066: stress (Pa)
14.067: surface tension (N/m)
14.068: temperature (°C)
14.069: temperature absolute (K)
14.070: temperature difference (K)
14.071: thermal capacity (J/K)
14.072: thermal conductivity (W/mK)
14.073: thermoelectric power (V/K)
14.074: time (s)
14.075: torque (Nm)
14.076: volume (m³)
14.077: volume flux (m³/s)
14.078: weight (N)
14.079: work (J)
14.1200: volume flux for meters (m³/h)
14.1201: volume flux for meters (1/ls)
15.xxx: entrance access
15.000: entrance access
16.xxx: character string
16.000: Character String (ASCII)
16.001: Character String (ISO 8859-1)
17.xxx: scene number
17.001: scene number
18.xxx: scene control
18.001: scene control
19.xxx: Date Time
19.001: date time
20.xxx: 1-byte
20.001: SCLO mode
20.002: building mode
20.003: occupied
20.004: priority
20.005: light application mode
20.006: light application area
20.007: alarm class
20.008: PSU mode
20.011: system error class
20.012: HVAC error class
20.013: time delay
20.014: wind force scale (0..12)
20.017: sensor mode
20.020: actuator connect type
20.021: cloud cover
20.022: power return mode
20.100: fuel type
20.101: burner type
20.102: HVAC mode
20.103: DHW mode
20.104: load priority
20.105: HVAC control mode
20.106: HVAC emergency mode
20.107: changeover mode
20.108: valve mode
20.109: damper mode
20.110: heater mode
20.111: fan mode
20.112: master/slave mode
20.113: status room setpoint
20.114: metering device type
20.115: hum dehum mode
20.116: enable H/C stage
20.120: ADA type
20.121: backup mode
20.122: start syncronization type
20.600: behavior lock/unlock
20.601: behavior bus power up/down
20.602: dali fade time
20.603: blink mode
20.604: light control mode
20.605: PB switch mode
20.606: PB action mode
20.607: PB dimm mode
20.608: switch on mode
20.609: load type
20.610: load type detection
20.611: converter test control
20.801: SAB except behavior
20.802: SAB behavior on lock/unlock
20.803: SSSB mode
20.804: blinds control mode
20.1000: communication mode
20.1001: additional information type
20.1002: RF mode selection
20.1003: RF filter mode selection
21.xxx: 8-bit set
21.001: general status
21.002: device control
21.100: forcing signal
21.101: forcing signal cool
21.102: room heating controller status
21.103: solar DHW controller status
21.104: fuel type set
21.105: room cooling controller status
21.106: ventilation controller status
21.107: combined status RTSM
21.601: lighting actuator error information
21.1000: RF communication mode info
21.1001: cEMI server supported RF filtering modes
21.1010: channel activation for 8 channels
22.xxx: 16-bit set
22.100: DHW controller status
22.101: RHCC status
22.102: combined status HVA
22.103: combined status RTC
22.1000: media
22.1010: channel activation for 16 channels
23.xxx: 2-bit set
23.001: on/off action
23.002: alarm reaction
23.003: up/down action
23.102: HVAC push button action
24.xxx:
24.001: Variable-Length ISO-8859-1 String
25.xxx: 2-nibble set
25.1000: busy/nak repetitions
26.xxx: 8-bit set
26.001: scene information
27.xxx: 32-bit set
27.001: bit-combined info on/off
28.xxx:
28.001: Unicode UTF-8 String
29.xxx: electrical energy
29.010: active energy (Wh)
29.011: apparant energy (VAh)
29.012: reactive energy (VARh)
30.xxx: 24 times channel activation
30.1010: activation state 0..23
206.xxx: 16-bit unsigned value & 8-bit enum
206.100: time delay & HVAC mode
206.102: time delay & DHW mode
206.104: time delay & occupancy mode
206.105: time delay & building mode
207.xxx: 8-bit unsigned value & 8-bit enum
207.600: Status Lighting Actuator
217.xxx: datapoint type version
217.001: DPT version
219.xxx: alarm info
219.001: alarm info
222.xxx: 3x 2-byte float value
222.100: room temperature setpoint
222.101: room temperature setpoint shift
225.xxx: scaling speed
225.001: scaling speed
225.002: scaling step time
229.xxx: 4-1-1 byte combined information
229.001: metering value (value,encoding,cmd)
230.xxx: MBus address
230.1000: MBus address
232.xxx: 3-byte colour RGB
232.600: RGB value 3x(0..255)
234.xxx: language code ISO 639-1
234.001: language code (ASCII)
235.xxx: Signed value with classification and validity
235.001: electrical energy with tariff
236.xxx: Prioritised Mode Control
236.001: priority control
237.xxx: configuration/ diagnostics
237.600: diagnostic value
238.xxx: configuration/ diagnostics
238.600: diagnostic value
240.xxx: positions
240.800: combined position
241.xxx: status
241.800: status sunblind & shutter actuator
242.xxx: status
242.600: colour xyY
244.xxx: Converter Status
244.600: DALI converter status
245.xxx: Converter test result
245.600: DALI converter test result
246.xxx: Battery Information
246.600: Battery Information
249.xxx: brightness colour temperature transition
249.600: brightness colour temperature transition
250.xxx: status
250.600: brightness colour temperature control
251.xxx: Colour RGBW
251.600: RGBW value 4x(0..100%)
252.xxx: Relative Control RGBW
252.600: RGBW relative control
254.xxx: Relative Control RGB
254.600: RGB relative control
255.xxx: F32F32
255.001: geographical location (longitude and latitude) expressed in degrees
275.xxx: F16F16F16F16
275.100: Temperature setpoint setting for 4 HVAC Modes
275.101: Temperature setpoint shift setting for 4 HVAC Modes

## Index_IfType (hidden)
Usb
IpTunnel
IpRouter

## Index_ObjType (hidden)
Switch
Dimming
Curtain
Value
EnableCtl

## Index_TgtType (hidden)
Switch
Dimming
Value
Scene